## MCC CABLE SCHDULE
SR. NO. | CABLE NO. | CABLE TAG | FEEDER NO | FROM TB NO | FROM FERRULE NO | FROM PANEL / JB NO | FROM PANEL / JB DESCRIPTION | SYSTEM VOLTAGE | KW RATING | Type | CABLE SIZE | CABLE TYPE | TO FERRULE NO | TO EQUIPMENT NO | TAG NOS. | TO TB NO. | TO EQUIPMENT DESCRIPTION | CABLE LENGTH (IN MTR.) | CABLE OD | ENTRY AVAILABLE AT PANEL / JB | SIZE SELECTED AT PANEL / JB | GLAND CAT NO AT PANEL / JB | SHROUD REQUIREMENT AT PANEL / JB | SHROUD CAT NO AT PANEL / JB | ENTRY AVAILABLE AT EQUIPMENT | SIZE SELECTED AT EQUIPMENT | GLAND CAT NO AT EQUIPMENT | SHROUD REQUIREMENT AT EQUIPMENT | SHROUD CAT NO AT EQUIPMENT | CABLE TRAY ROUTING | REMARK | 50W | 100W | 50W | 100W | SCOPE
Note on D7: Author: KEEP BLANK WILL BE FILLED AFTER RECEIPT OF VENDOR DRAWING
Note on E7: Author: KEEP BLANK WILL BE FILLED AFTER RECEIPT OF VENDOR DRAWING
Note on G7: Author: MANUAL ENTRY
Note on H7: Author: FROM PROJECT INFORMATION UI
Note on I7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 415VAC 230 VAC 110 VAC 4-20 mA
Note on P7: Author: MOTOR TAG THIS WILL COME FROM LOAD LIIST
Note on R7: Author: THIS WILL COME FROM LOAD LIST
Note on U7: FOR PANEL SIDE, PLATE WILL BE DEFAULT ENTRY
Note on V7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MANUAL SELECTION
Note on W7: SUMMARY TO BE CRAETED BASED ON THIS COLUMN DATA
Note on X7: DEFAULT VALUE WILL BE NO
Note on Y7: Author: Do not fill / edit anything in this coloumn AUTO SELECTION
Note on Z7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MANUAL SELECTION
Note on AA7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MANUAL SELECTION
Note on AB7: SUMMARY TO BE CRAETED BASED ON THIS COLUMN DATA
Note on AC7: THIS WILL BE POPUKATED FROM ELECTRICAL LOAD LIST
Note on AD7: Author: Do not fill / edit anything in this coloumn AUTO SELECTION
Note on AE7: Author: DEFAULT HIDE

## Dropdowns (hidden)
0.625" ET
0.75" ET
1" ET
1.25" ET
1.5" ET
2" ET
2.5" ET
3" ET
3.25" ET
3.5" ET
4" ET
4.5" ET
40 MM
42 MM
70 MM
3.75" ET
M28
M40
M42
M70
M16
M20
M25
M32
M50
M63
M75
M82
M90
M100
M115
1/2" NPT
3/4" NPT
1" NPT
1.25" NPT
1.5" NPT
2" NPT
2.5" NPT
3" NPT
3.5" NPT

## GLAND SELEC. INPUT & NOTES SHT (hidden)
INSTRUCTIONS & NOTES FOR SELECTION OF WEATHER PROOF DOUBLE COMPRESSION CABLE GLANDS USING THIS CABLE SCHEDULE
Notes :
1 | This Excel is for selection of Weather Proof Double compression cable glands for Armoured / Unarmoured cables.
2 | This Excel has been prepared with Standard cable gland CAT No's of make Braco & Comet.
3 | This Excel can be used for selection of all type of cable entries i.e. ET, Metric, NPT.
4 | This Excel has been prepared with cable gland MOC of Nickel Plate Brass & SS304.
(SS304 MOC for Make Braco make only.)
Instructions to use :
1 | Select the cable gland Make & MOC as per the project requirement. (Discuss with respective buyer & PM for the make)
|  | 1 | SELECT GLAND MAKE : | BRACO
|  | 2 | SELECT GLAND MOC : | Ni PLATED BRASS
2 | Please do not shift any rows / coloumns in cable schedule sheet.
3 | Cable size description should be as follows do not change the format/sequence(ex. Space) of the description. It should be always
end with either "ARMOURED CABLE" or "UNARMOURED CABLE".
| Ex . | a) "3C x 2.5 SQ.MM. CU. XLPE/PVC ARMOURED CABLE"
b) "3C x 2.5 SQ.MM. CU. XLPE/PVC UNARMOURED CABLE"
c) "1PR X 1.0 SQ.MM. CU. XLPE/PVC ARMOURED CABLE"
4 | Fill the cable types & OD below. ( Take exact OD from test report(recommended). If exact OD not available mention OD with specificied
tolerance in final datasheet.)
|  | Sr.No | Cable Size (Discription shall be same as cable schedule) | Cable OD
|  | 1 | 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | 17
|  | 2 | 3C X 6 SQ.MM. AL. XLPE ARMOURED CABLE | 20
|  | 3 | 3C X 10 SQ.MM. AL. XLPE ARMOURED CABLE | 21
|  | 4 | 3C X 16 SQ.MM. AL. XLPE ARMOURED CABLE | 21
|  | 5 | 3C X 35 SQ.MM. AL. XLPE ARMOURED CABLE | 24.5
|  | 6 | 3C X 70 SQ.MM. AL. XLPE ARMOURED CABLE | 30.5
|  | 7 | 3C X 95 SQ.MM. AL. XLPE ARMOURED CABLE | 34
|  | 8 | 3.5C X 120 SQ.MM. AL. XLPE ARMOURED CABLE | 42
|  | 9 | 3.5C X 35 SQ.MM. AL. XLPE ARMOURED CABLE | 28
|  | 10 | 3.5C X 70 SQ.MM. AL. XLPE ARMOURED CABLE | 35
|  | 11 | 3.5C X 95 SQ.MM. AL. XLPE ARMOURED CABLE | 39
|  | 12 | 4C X 10 SQ.MM. AL. XLPE ARMOURED CABLE | 22
|  | 13 | 6P X 1 SQ.MM. CU. ARMOURED CABLE | 20
|  | 14 | 7C X 1.5 SQ.MM. CU. XLPE ARMOURED CABLE | 18
5 | In "cable schedule" sheet "FROM / TO SIDE ENTRY AVAILABLE" coloumn fill the availabe Entry as per the Equipment / Instrument datasheet.
6 | In "cable schedule" sheet "FROM / TO SIDE SIZE SELECTED" coloumn if the entry available is "Plate" Select the ET size (start from minimum size to
maximum size to obtain the Gland CAT No. and if not plate select the same size as Available entry.
7 | If the above Instructions followed properly Gland CAT would have been generated automatically by now. If not it might be non standard requirement
please select the cable gland as per the respective cable gland catalogues.
8 | After that In "cable schedule" Sheet "FROM / TO SIDE SHROUD REQUIREMENT" Coloumn Select either "Yes" or "No" as per the requirement.
(Note PVC Shroud shall be used for all Glands which are outside MCC / Control Room)
9 | After Selection of Shroud requirement Shroud CAT No. would have been generated automatically by now.
10 | After completion of All cable gland selection Hide the "To be hide" coloumn while submitting to client.