## COVER
THERMAX LIMITED
HEATING
PUNE — 411 019
| TITLE |  | VOLTAGE DROP CALCULATION
CLIENT
CONSULTANT
PROJECT
THERMAX O.C. NO.
THERMAX DOC. NO. / CLIENT DOC. NO.
| R0 | 05-11-2024 | ISSUED FOR APPROVAL | SP | JJ | RBB
| REV NO. | DATE | DESCRIPTION | PREPD BY | CHKD BY | APPD. BY

## REVISION
REV. | DATE | REVISION DESCRIPTION
R0 | 01-08-2024 | ISSUED FOR APPROVAL

## VOLTAGE DROP CALCULATION
SR.NO. | FROM | LOAD DESCRIPTION / TO | KW | SUPPLY PHASE | STARTER | SUPPLY VOLTAGE | EFFICIENCY (%) | COS φ (RUN) | SIN φ (RUN) | COS φ (START) | SIN φ (START) | I (RUN) in Amp. | I (START) in Amp | MOC | Number Of Run(s) | CABLE SIZE (Sq.mm) | RESISTANCE / Mtr | REACTANCE / Mtr | APX. LENGTH (m) | V.D (RUN) | V.D (START) | % VD at Running | % VD at Start | Selected cable Current carrying capacity (Amp) | Derating Factor (Note-1) | Final Current carrying capacity (Amp) | Cable Selected Status
Note on M2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Compare with G in cable data
Note on W2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Form UI higher limit will come if % voltage drop crosses the allowed limit then specify Unsafe in cable selected status and if its withing limit then safe Reply: Motor Voltage Drop During Running
Note on X2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Form UI higher limit will come if % voltage drop crosses the allowed limit then specify Unsafe in cable selected status and if its withing limit then safe Reply: Motor Voltage Drop During Starting

## Motor Data
Kw | A | Number_of_Pole | IE1_Percent | IE2_Percent | IE3_Percent | Speed_RPM
0.37 | 1.2 | 2 | 66.1 | 72.2 | 75.5 | 3000
0.55 | 1.6 | 2 | 69.1 | 74.8 | 78.1 | 3000
0.75 | 2 | 2 | 72.1 | 77.4 | 80.7 | 3000
1.1 | 2.8 | 2 | 75 | 79.6 | 82.7 | 3000
1.5 | 3.7 | 2 | 77.2 | 81.3 | 84.2 | 3000
2.2 | 5 | 2 | 79.7 | 83.2 | 85.9 | 3000
3.7 | 8 | 2 | 82.7 | 85.5 | 87.8 | 3000
5.5 | 11 | 2 | 84.7 | 87 | 89.2 | 3000
7.5 | 15 | 2 | 86 | 88.1 | 90.1 | 3000
11 | 21.5 | 2 | 87.6 | 89.4 | 91.2 | 3000
15 | 29 | 2 | 88.7 | 90.3 | 91.9 | 3000
18.5 | 35 | 2 | 89.3 | 90.9 | 92.4 | 3000
22 | 41.5 | 2 | 89.9 | 91.3 | 92.7 | 3000
30 | 54 | 2 | 90.7 | 92 | 93.3 | 3000
37 | 67 | 2 | 91.2 | 92.5 | 93.7 | 3000
45 | 80 | 2 | 91.7 | 92.9 | 94 | 3000
55 | 95 | 2 | 92.1 | 93.2 | 94.3 | 3000
75 | 130 | 2 | 92.7 | 93.8 | 94.7 | 3000
90 | 150 | 2 | 93 | 94.1 | 95 | 3000
110 | 185 | 2 | 93.3 | 94.3 | 95.2 | 3000
125 | 209 | 2 | 93.4 | 94.5 | 95.3 | 3000
132 | 220 | 2 | 93.5 | 94.6 | 95.4 | 3000
160 | 265 | 2 | 93.8 | 94.8 | 95.6 | 3000
200 | 340 | 2 | 94 | 95 | 95.8 | 3000
250 | 425 | 2 | 94 | 95 | 95.8 | 3000
315 | 536 | 2 | 94 | 95 | 95.8 | 3000
355 | 604 | 2 | 94 | 95 | 95.8 | 3000
375 | 604 | 2 | 94 | 95 | 95.8 | 3000
0.37 | 1.4 | 4 | 65.1 | 70.1 | 73 | 1500
0.55 | 1.7 | 4 | 69.1 | 75.1 | 78 | 1500
0.75 | 2.2 | 4 | 72.1 | 79.6 | 82.5 | 1500
1.1 | 2.9 | 4 | 75 | 81.4 | 84.1 | 1500
1.5 | 3.8 | 4 | 77.2 | 82.8 | 85.3 | 1500
2.2 | 5.1 | 4 | 79.7 | 84.3 | 86.7 | 1500
3.7 | 8.1 | 4 | 82.7 | 86.3 | 88.4 | 1500
5.5 | 11.4 | 4 | 84.7 | 87.7 | 89.6 | 1500
7.5 | 15.4 | 4 | 86 | 88.7 | 90.4 | 1500
11 | 22 | 4 | 87.6 | 89.8 | 91.4 | 1500
15 | 30 | 4 | 88.7 | 90.6 | 92.1 | 1500
18.5 | 36 | 4 | 89.3 | 91.2 | 92.6 | 1500
22 | 43 | 4 | 89.9 | 91.6 | 93 | 1500
30 | 56 | 4 | 90.7 | 92.3 | 93.6 | 1500
37 | 69 | 4 | 91.2 | 92.7 | 93.9 | 1500
45 | 84 | 4 | 91.7 | 93.1 | 94.2 | 1500
55 | 99 | 4 | 92.1 | 93.5 | 94.6 | 1500
75 | 134 | 4 | 92.7 | 94 | 95 | 1500
90 | 164 | 4 | 93 | 94.2 | 95.2 | 1500
110 | 204 | 4 | 93.3 | 94.5 | 95.4 | 1500
125 | 234 | 4 | 93.4 | 94.6 | 95.5 | 1500
132 | 247 | 4 | 93.5 | 94.7 | 95.6 | 1500
160 | 288 | 4 | 93.8 | 94.9 | 95.8 | 1500
200 | 348 | 4 | 94 | 95.1 | 96 | 1500
250 | 435 | 4 | 94 | 95.1 | 96 | 1500
315 | 548 | 4 | 94 | 95.1 | 96 | 1500
355 | 618 | 4 | 94 | 95.1 | 96 | 1500
375 | 653 | 4 | 94 | 95.1 | 96 | 1500
0.37 | 1.4 | 6 | 63 | 69 | 71.9 | 1000
0.55 | 1.9 | 6 | 67 | 72.9 | 75.9 | 1000
0.75 | 2.3 | 6 | 70 | 75.9 | 78.9 | 1000
1.1 | 3.2 | 6 | 72.9 | 78.1 | 81 | 1000
1.5 | 4 | 6 | 75.2 | 79.8 | 82.5 | 1000
2.2 | 5.5 | 6 | 77.7 | 81.8 | 84.3 | 1000
3.7 | 8.8 | 6 | 80.9 | 84.3 | 86.5 | 1000
5.5 | 12.7 | 6 | 83.1 | 86 | 88 | 1000
7.5 | 16.7 | 6 | 84.7 | 87.2 | 89.1 | 1000
11 | 23 | 6 | 86.4 | 88.7 | 90.3 | 1000
15 | 30.5 | 6 | 87.7 | 89.7 | 91.2 | 1000
18.5 | 37.5 | 6 | 88.6 | 90.4 | 91.7 | 1000
22 | 44 | 6 | 89.2 | 90.9 | 92.2 | 1000
30 | 59 | 6 | 90.2 | 91.7 | 92.9 | 1000
37 | 72 | 6 | 90.8 | 92.2 | 93.3 | 1000
45 | 87 | 6 | 91.4 | 92.7 | 93.7 | 1000
55 | 107 | 6 | 91.9 | 93.1 | 94.1 | 1000
75 | 145 | 6 | 92.6 | 93.7 | 94.6 | 1000
90 | 175 | 6 | 92.9 | 94 | 94.9 | 1000
110 | 214 | 6 | 93.3 | 94.3 | 95.1 | 1000
125 | 245 | 6 | 93.4 | 94.4 | 95.2 | 1000
132 | 257 | 6 | 93.5 | 94.6 | 95.4 | 1000
160 | 315 | 6 | 93.8 | 94.8 | 95.6 | 1000
200 | 370 | 6 | 94 | 95 | 95.8 | 1000
250 | 463 | 6 | 94 | 95 | 95.8 | 1000
315 | 583 | 6 | 94 | 95 | 95.8 | 1000
355 | 657 | 6 | 94 | 95 | 95.8 | 1000
375 | 694 | 6 | 94 | 95 | 95.8 | 1000

## Cable Data
noofcore | sizesqmm | make | odmm | weightofcable | urrentground | currentair | cabletype | x | r | dbl_area | MOC
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 4 | Polycab | 16 | 580 | 43 | 36 | 2XWY | 0.0927 | 5.9 | 201 | Copper
3 | 6 | Polycab | 17 | 680 | 54 | 47 | 2XWY | 0.0884 | 3.94 | 227 | Copper
3 | 10 | Polycab | 19 | 750 | 72 | 62 | 2XWY | 0.0837 | 2.34 | 283 | Copper
3 | 16 | Polycab | 21 | 750 | 73 | 70 | A2XFY | 0.0808 | 2.44 | 346 | Aluminium
3 | 16 | Polycab | 21 | 750 | 73 | 70 | A2XFY | 0.0808 | 2.44 | 346 | Aluminium
3 | 25 | Polycab | 23 | 990 | 94 | 96 | A2XFY | 0.0805 | 1.54 | 415 | Aluminium
3 | 35 | Polycab | 25 | 1150 | 113 | 117 | A2XFY | 0.0783 | 1.11 | 491 | Aluminium
3 | 50 | Polycab | 27.5 | 1400 | 133 | 142 | A2XFY | 0.075 | 0.82 | 594 | Aluminium
3 | 70 | Polycab | 32 | 1950 | 164 | 179 | A2XFY | 0.074 | 0.567 | 804 | Aluminium
3 | 95 | Polycab | 37.5 | 2300 | 196 | 221 | A2XFY | 0.0724 | 0.41 | 1104 | Aluminium
3 | 95 | Polycab | 37.5 | 2300 | 196 | 221 | A2XFY | 0.0724 | 0.41 | 1104 | Aluminium
3 | 120 | Polycab | 39.5 | 2700 | 223 | 257 | A2XFY | 0.0712 | 0.324 | 1225 | Aluminium
3 | 150 | Polycab | 43.5 | 3200 | 249 | 292 | A2XFY | 0.0716 | 0.264 | 1485 | Aluminium
3 | 150 | Polycab | 43.5 | 3200 | 249 | 292 | A2XFY | 0.0716 | 0.264 | 1485 | Aluminium
3 | 185 | Polycab | 48.5 | 4200 | 282 | 337 | A2XFY | 0.0718 | 0.21 | 1847 | Aluminium
3 | 185 | Polycab | 48.5 | 4200 | 282 | 337 | A2XFY | 0.0718 | 0.21 | 1847 | Aluminium
3 | 240 | Polycab | 53 | 5100 | 326 | 399 | A2XFY | 0.071 | 0.16 | 2205 | Aluminium
3 | 240 | Polycab | 53 | 5100 | 326 | 399 | A2XFY | 0.071 | 0.16 | 2205 | Aluminium
3 | 300 | Polycab | 57.5 | 5900 | 367 | 455 | A2XFY | 0.0705 | 0.128 | 2595 | Aluminium
3 | 300 | Polycab | 57.5 | 5900 | 367 | 455 | A2XFY | 0.0705 | 0.128 | 2595 | Aluminium
3 | 300 | Polycab | 57.5 | 5900 | 367 | 455 | A2XFY | 0.0705 | 0.128 | 2595 | Aluminium
3 | 300 | Polycab | 57.5 | 5900 | 367 | 455 | A2XFY | 0.0705 | 0.128 | 2595 | Aluminium
3.5 | 25 | Polycab | 25.5 | 1050 | 94 | 96 | A2XFY | 0.0805 | 1.54 | 510 | Aluminium
3.5 | 35 | Polycab | 26.5 | 1200 | 113 | 117 | A2XFY | 0.0783 | 1.11 | 551 | Aluminium
3.5 | 50 | Polycab | 29.5 | 1500 | 133 | 142 | A2XFY | 0.075 | 0.82 | 683 | Aluminium
3.5 | 70 | Polycab | 34 | 2050 | 164 | 179 | A2XFY | 0.074 | 0.567 | 907 | Aluminium
3.5 | 95 | Polycab | 38 | 2450 | 196 | 221 | A2XFY | 0.0724 | 0.41 | 1134 | Aluminium
3.5 | 150 | Polycab | 45 | 3350 | 249 | 292 | A2XFY | 0.0716 | 0.264 | 1590 | Aluminium
3.5 | 185 | Polycab | 50 | 4500 | 282 | 337 | A2XFY | 0.0718 | 0.21 | 1963 | Aluminium
3.5 | 120 | Polycab | 41 | 2800 | 223 | 257 | A2XFY | 0.0712 | 0.324 | 1320 | Aluminium
3.5 | 120 | Polycab | 41 | 2800 | 223 | 257 | A2XFY | 0.0712 | 0.324 | 1320 | Aluminium
3.5 | 150 | Polycab | 45 | 3350 | 249 | 292 | A2XFY | 0.0716 | 0.264 | 1590 | Aluminium
3.5 | 185 | Polycab | 50 | 4500 | 282 | 337 | A2XFY | 0.0718 | 0.21 | 1963 | Aluminium
3.5 | 240 | Polycab | 56 | 5450 | 326 | 399 | A2XFY | 0.071 | 0.16 | 2462 | Aluminium
3.5 | 240 | Polycab | 56 | 5450 | 326 | 399 | A2XFY | 0.071 | 0.16 | 2462 | Aluminium
3.5 | 300 | Polycab | 61 | 6400 | 367 | 455 | A2XFY | 0.0705 | 0.128 | 2921 | Aluminium
3.5 | 300 | Polycab | 61 | 6400 | 367 | 455 | A2XFY | 0.0705 | 0.128 | 2921 | Aluminium