## COVER
THERMAX LIMITED
HEATING
PUNE — 411 019
| TITLE |  | POWER CUM PLC PANEL SPECIFICATION
CLIENT
CONSULTANT
PROJECT
THERMAX O.C. NO.
THERMAX DOC. NO. / CLIENT DOC. NO.
| R0 |  | ISSUED FOR APPROVAL
| REV NO. | DATE | DESCRIPTION | PREPD. BY | CHKD. BY | APPD. BY | 5.5

## MCC CUM PLC PANEL
PANEL SPECIFICATION
SR.No. | DESCRIPTION | OUTPUT
1 | ITEM | Power cum PLC Panel
2 | ENCLOSURE MAKE | Thermax approved vendor
3 | REFERENCE DOCUMENTS
| Electrical Load List | PZZXXXDCXX
| Single Line Diagram | PZZXXXDCXX
| Electrical Control Schemes | PZZXXXDCXX
4 | FEEDER SWITCHGEAR TYPE | Type II Co-ordination Fuse
5 | SUPPLY REQUIREMENTS
| System (voltage) | 415 VAC, +/-10%, 3-Phase, 4 wire
| Frequency | 50 Hz, +/-5% - 1sec
| Fault Level | Min 35 kA for 1 sec
| Utility voltage | 230 VAC, 1-Phase, 2 wire
| Control voltage | 230 VAC, 1-Phase, 2 wire
| Frequency | 50 Hz
6 | SITE DETAILS
| Project Location | Pune
| Ambient Temperature (Max) | 45 Deg.C
| Ambient Temperature (Min) | 35 Deg.C
| Electrical Design Temperature | 45 Deg.C
| Seismic Zone | 2
| Area Classification | Safe Area
| Altitude | 750 Meter
| Humidity ( Max) | 85%
| Humidity ( Man) | 35%
| Humidity Average | 65%
| Humidity Performance. | 65%
7 | CONSTRUCTION
| Design Standard, Manufacturers Standdard & Testing Standard | IEC 61439
| IP Protection | IP 52
| Type of Construction for Board | Single front
| Panel Front Type | From IA (Non-Compartmental)
| Panel Incoming Feeder Drawout Type | Non Drawout
| Panel Outgoing Feeder Drawout Type | Non Drawout
| Panel Construction Type | Intelligent
| Panel Mounting | Base frame
| Height of Base Frame | 100mm
| Height Of Panel | 2100mm
| Marshalling Section (Compartmental panel only) | a) Min width 400 mm & Above b) Separate Marshaling for each shiping section with Partition c) Signal from MCC to PLC DI/DO/AI/AO with Separate TB. d) DI, DO TB to be mounted on separate column e) Signal from MCC to Field with Separate TB.
| Cable Alley Section (Compartmental panel only) | Not Applicable
8 | THICKNESS
| Component Mounting Plate | 2.0mm
| Door | 1.6mm
| Top & Side | 1.6mm
| Gland Plate | 3.0mm
| Gland Plate Type | Drilled - Removable
| Cable Entry Position | Top
| Busbar Chamber Position | NA
| Earth Busbar Position | Bottom
| Seperation between Power & Control busbar | Acrylic
9 | PAINTING / POWDER COATING
| Paint Shade for Interior and Exterior | RAL 7032
| Paint Shade for Component Mounting Plate | RAL 2000
| Paint Shade for Base Frame | Black
| Paint Coating Thickness | 60-70 Microns (for domestic order) & 100 Microns (for Export order) / As per Client specification
| Standard for Pretreatment | - Panel Shall Be Degreased And Derusted (7 Tank Pretreatment) - Panel Shall Be Powder Coated. OR - OEM standard for pretreatment.
General Requirments For Construction
10 | BUSBAR
A | POWER BUS
| Type of Main Busbar | IEC 61439
| Material of construction | Aluminium
| Current Density | 0.8A/sq.mm
| Busbar Size & Rating | 1R x 65 X 10 mm
| Heat shrinkAble PVC sleeves | Red,yellow,blue,black
B | CONTROL BUS
| Type of Main Busbar | IEC 61439
| Material of construction | Aluminium
| Current Density | 0.8A/sq.mm
| Busbar Size & Rating | VTS
| Heat ShrinkAble PVC sleeves | Red, black
C | EARTH BUS
| Type of Main Busbar | IEC 61439
| Material of Construction | Aluminium
| Current Density | 0.8A/sq.mm
| Busbar Size & Rating | 1R x 30 X 10 mm
| Busbar Mounting | TOP
| Door Earthing | Through Separate Stud With Yellow-Green PVC stranded copper wire (2.5 sq.mm)
| Instrument Earth | 1. Dark Green PVC Copper Wire 0.5/1 Sq.mm & Copper Busbar 2. Every VFD section shall have isolated Isntrument Earth busbar
General Note Busbar & Insulation Materials
11 | PANEL WIRING
| Power wiring ( L1, L2, L3, N) | Red,Yellow,Blue,Black
| Cable Size | Min.2.5 sq.mm
| Control Wiring ( P, N) | Grey,Black
| Cable Size | 1 Sq.mm
| 24 VDC Wiring (+, - ) | Orange,White
| Cable Size | 0.75 Sq.mm
| Analog Signal Wiring (+, - ) | Brown,White Shielded Cable
| Cable Size | 0.5 Sq.mm
| CT Wiring | Red,Yellow,Blue,Black
| Cable Size | 2.5 Sq.mm
| Cable Insulation (PVC) | Flame Retardant Low Smoke
| Common Requirement | 660/1100 V Grade PVC insulated, FR/FRLS, Multistranded, Copper, Flexible cable identified with colour code
| Air Clearance between Phase to Phase Bus | 25 mm
| Air Clearance between Phase to Neutral Bus | 19 mm
General Note Internal Wiring
12 | PANEL MOUNTEED
A | PANEL MOUNTED PUSH BUTTONS & COLOURS
| Start Push Button | Green
| Forward Start Push Button | Yellow
| Reverse Start Push Button | Yellow
| Stop Push Button | Rad
| Emergency Stop Push Button | Mushroom headed Stayput ( Key to release) Red Colour
| Speed Increase Push Button | Blue
| Speed Decrease Push Button | Yellow
| Potentiometer | Not-applicable
| Alarm Annunciator | Not-applicable
| Alarm acknowledge | NA
| Test | Black
| Reset | NA
B | PANEL MOUNTED INDICATING LAMPS & COLOURS
| Run | Green
| Stop | Red
| Trip | Amber
C | TERMINAL BLOCK CONNECTORS
| Power Terminal Clipon | Min.4 Sq.mm Clipon Type
| Power Terminal Busbar Type | Above 4 sq.mm Busbar Type
| Control Terminal | Min.4 Sq.mm Clipon Type
| Spare Terminal | 10%
13 | IDENTIFICATION OF COMPONENTS
| Ferrule | Straight ferrule
| Ferrule Note | Printed Ferrules-Black Letters On White Sleeves
| Device Identification of components | PVC sticker with black letters
| Name Plate Details for feeder | Feeder Tag, compartment, KW, feeder name, etc Engraved label
| Name Plate Details for Instruments | Instrument Tag, instrument name, etc Engraved label
14 | ACCESSORIES
A | METERING INSTRUMENTS FOR INCOMER
| Digital Meter | Multifunction meter
| Analog Meter | Ammeter with ASS
| Communication Protocol | Modbus
B | CURRENT TRANSFORMER INCOMER
| Current Transformer Coating | Cast resin
| Current Transformer Quantity | Three
| Current Transformer Configruration | All Phase with CT
C | INCOMER TYPE
| Panel Incomer Type | Upto 630A , 3 Pole MCCB Above 630A, 4 Pole EDO ACB
| Incomer ON Indication lamp | Not Applicable
| Incomer OFF Indication lamp | Red
| Incomer Trip Indication lamp | Amber
| ACB Spring Charge Indication lamp | Blue
| ACB Service Indication lamp | Not Applicable
| Trip Circuit Healthy Indication lamp | White
D | CONTROL TRANSFORMER
| Control Transformer Primary voltage | 230 VAC, 1-Phase, 2 wire
| Control Transformer Secondary voltage | 230 VAC, 1-Phase, 2 wire
| Control Transformer Coating | Tape Wound
| Control Transformerr Quantity | One
| Control Transformer Configruration | Single
| Control Transformer Type | Industrial control Step down transformer
E | METERING INSTRUMENTS FOR FEEDERS
| Digital Meter | NA
| Analog Meter | Ammeter with ASS
| Communication Protocol | NA
F | CURRENT TRANSFORMER FEEDER
| Current Transformer | 37kW and above
| Current Transformer Coating | Cast resin
| Current Transformer Quantity | One
| Current Transformer Configruration | Y-Phase with CT
G | FEEDER SELECTION & COMPONENTS
| DOL Feeder | As per Control scheme
| RDOL Feeder | As per Control scheme
| Star-Delta Feeder | As per Control scheme
| VFD Feeder | As per Control scheme
| VFD Input/Output Chock | As per Control scheme
| VFD Speed Feedback | As per Control scheme
| VFD Current Feedback | As per Control scheme
| Local - Remote Selector Switch | As per Control scheme
14 | PANELS OTHERS
| Cooling Fans | Applicable
| Louvers and Filters | Applicable
15 | SPARES
Commissioning Spare
Two Year Operational Spare
16 | PPROJECT SPECIFIC NOTES
17 | MAKE OF COMPONENTS | Approved make list to be provided by TL Material team. Approved make list shall supercede panel builder std.
A | Switchgear
| MCB/MPCB/MCCB | Siemens/Schneider/L&T
| Isolating/Changeover Switch | Siemens/Schneider/L&T
| HRC/Semiconductor Fuses | Siemens/Schneider/L&T
| Contactors/Overload Relays | Siemens/Schneider/L&T
| Timer | Siemens/Schneider/L&T/EAPL
B | Controlgear
| Indicating Lamp shall be of LED type | Teknic/Siemens/Jai Balaji/Schneider
| Pushbutton | Teknic/Siemens/Jai Balaji/Schneider
| Selector Switch | Teknic/Siemens/Jai Balaji/Schneider/Salzer
| Ammeter Selector switch | Salzer/kAycee
| Voltmeter Selector switch | Salzer/kAycee
C | Meter
| Voltmeter | AE/Rishabh/Meco
| Ammeter | AE/Rishabh/Meco
| KWH meter | Conzerv/Selectron/Rishabh/Siemens/Schneider
| Multifunction meter (Load manager) | Conzerv/Selectron/Rishabh/Siemens/Schneider
D | Cable
| PVC Cable | Polycab/Finolex/RR Cable
| Shielded Cables | LAPP/Hellu/Local
E | Accessories
| Current Transformer | AE/Starlit/Precise/kAppa
| Control Transformer | AE/Starlit/Precise/kAppa/JD
| Hooter(Electronic) | Captain/Cands/Yashmun
| Power supply Unit | Siemens/Allen-Bradley/Schneider
| Auxiliary Relay Board | UL/Phoenix with Omron relays with indicating LED
| Alarm Annunciator | Proton/Minilec/IIC/Instalarm
| Signal Distributor/Convertor | Masibus/P&F
| Cable Channel | SFX/Salzer
| Terminals | Elmex/Connectwell/Phoenix/Salzer
| Door Limit Switch | Any make
| Door Lock | Any make
| End Lugs | Any make
| CFL/Tubelight | Philips
| Utility Socket | Any make
| Fan | Any make
| Filter | Any make
| Potentiometer | Any make
F | Panel Mounted Instruments
| Temperature Indicator | Fuji/Yokogawa/Selectron/Artech controller
| Temperature Switch | Fuji/Yokogawa/Selectron/Artech controller
| PID Controller | Fuji/Yokogawa/Selectron
| Flow totaliser | Masibus/Nishko/Artech/Yokogawa
| Hour meter | Masibus/Nishko/Artech
| VFD | Danfoss/Siemens/ABB
G | PLC
| PLC | Siemens/Allen-Bradley/Schneider/Honeywell
| SCADA Software | Siemens/Allen-Bradley/Schneider/Honeywell
| PC with Monitor | DELL/HP
| Printer | HP
| Ethernet Switch | Phoenix/Datalink
| UPS | Champion/APC-Emerson
18 | DOCUMENTATION
A | With Quotation
Deviation and Clarification Sheet
Technical offer with detail BOM
B | Engineering approvals prior to manufacturing.
Panel GA Drawing
Panel Electrical Wiring Drawing
Panel Components BOM & Details
Test Certificates ( Short Circuit, IP Protection,etc)
Heat load and Cooling Calculation
Control Transformar VA Calculation
Busbar sizing calculation
C | Client Approvals prior to manufacturing.
Electrical drawing & Panel GA
Detail BOM for Panel components
D | Before Dispatch of Panel
Final as-built electrical drawing & Panel GA (CAD & PDF copy)
O & M manual - Instrument, PLC hardware, Program etc
Software Backup for PLC & SCADA Program, PPT (If Applicable)
As built BOM for Panel components
Parameter/Setpoint List - For Panel mounting components like VFD, Softstarter, ACB/MCCB, OLR, Protection Relay etc.
E | Applicable Deliverables
Panel GA Drawing
Panel Electrical Wiring Drawing
Panel Components BOM & Details
Test Certificates ( Short Circuit, IP Protection,etc)
Heat load and Cooling Calculation
Control Transformar VA Calculation
19 | GENERAL NOTES:
A | Construction / Lifting arrangement
Maximum panel length for shipping / transportation purpose shall be 3 meters. (i.e. total panel length shall be divided by 3 meters for ease of shipping / transportation).
Removable Lifting Eye Bolts / Lifting Angle with lifting Hooks must be provided for each Shipping / Transportation Section.
Busbar couplers with required hardware shall be provided by vendor for each shipping / transportation section.
Vendor to provide male-female connector(s) for all Interconnecting control & signal wiring / cabling for each shipping / Interconnecting wiring / cabling to be specifically identified & shall be rolled in suitable / applicable section after FAT / inspection, before packing / during transportation. Interconnecting wiring / cabling to be specifically identified & shall be rolled in suitable / applicable section after FAT / inspection, before packing / during transportation. transportation sections
Dust And Vermin Proof, Floor mounted, Free Standing, Front and rear access for maintanance, concealed hinges for all doors.
C | Switchgear details
Fan + filters are provided in VFD compartment.
DP MCB is provided for control circuit isolation of motor feeder.
Run/Trip signal potential free contacts are provided and provision for Start/Stop cmd from control system is provided for each motor feeder.
VFD shall be part of MCC panel assembly.
Switchgear assembly shall be as per IS 8623/IEC 60439.
Thermostat and Panel Space heater (for Compartmental panel only).
3 pin service euro socket with mcb 5A to be provided.
Mettalic Drawing Pocket shall be provided inside the door.
Neoprene rubber Gaskets are provided between adjacent panels, doors and removable covers.
All busbars and live part shall be shrouded with transparent acrylic sheet.
Power and instrument wires should have separate routing wherever possible.
Please note supplier should mention the motor tag number with description on the applicable Power, control and Marshalling wiring diagram.
Switchgear selection mentioned into the SLD document is inline w.r.t. TL approved siemens make selection chart. However, Other make switchgear selection. Kindly consult with TL Engg.
Control schematic diagram are provided for reference only. Aux. contactor & aux. contact blocks shall be considered as per actual requirement during detail engg. vendor to ensure requirement during pre-bid only.
MCC Panel & VFD heat load claculations to be furnished in separate document & send for approval.
Regarding selection for VFD/Soft-starter kindly concern with TL engineering. (VFD/Fuse/MCCB etc.)
Vendor to cross checked the VFD model with OEM before PO finalisation.
Vendor to provide Operation and maintenance manual, As built drawing on completion of the job.
For lambien grate boiler- (mentioned as RG for product name), Fuel feeder VFD selection shall be one stage higher than VFD kW with heavy duty application. Ex. If motor is 1.1kW, VFD shall be 1.5kW heavy duty. With this note kindly refer Items for MCC panel BOM for final VFD details
Supplier has to submit parameter list with drawing for approval for panel mount items like Controller/indicator, VFD, softstarter etc
All switchgear like CB, Relay, Timer settings shall be done by panel vendor at the time of panel internal testing.
Vendor to consider AS-BUILT / any Modification / any Add on required at site - drg. & documents in his scope of detailing without any commercial implication to Thermax Ltd. This need to be covered / complied as base offer from vendor
20 | Inspection Requirements
Vendor To Provide Internal Test Report Before Inspection Call.
Inspection By Thermax or Customer
Internal Agency-Q.C Engrs-Thermax Ltd
After Fabrication Prior To Painting
After Painting
After Wiring Assembly
1.5kv HV For 1 Minute
Insulation Test With 500v (Megger Test)
Functional Test Of The Control System
External- (If Applicable)
21 | Special Notes
If panels are having multiple shipping / transportation sections & interconnecting wiring / cabling are kept in rolled conditions (after FAT / Inspection) in any of the specific section then, panel vendor has to arrange his Technician / Electrician for connecting those rolled wires /cables to required section at site without any Time & commercial impact to Thermax Ltd.
22 | PUNCHING DETAILS
A | Punching Details for Boiler
Model :
Fuel :
Year :
Power Supply : VAC, Phase, Hz
Control Supply : VAC, Phase, Hz
Evaporation : Kg/Hr
Output : MW
Connected Load : KW
Design Pressure : Kg/cm2 (g) / Bar
B | Punching Details for Heater
Model :
Fuel :
Year :
Power Supply : VAC, Phase, Hz
Control Supply : VAC, Phase, Hz
Evaporation : Kcal/Hr
Output : MW
Connected Load : KW
Temperature: Deg.C

## PLC SPECIFICATION
PLC PANEL SPECIFICATION
SR.No. | DESCRIPTION | OUTPUT
1 | ITEM | Power cum PLC Panel
2 | ENCLOSURE MAKE | Thermax approved vendor
3 | REFERENCE DOCUMENTS
| Electrical Load List | PZZXXXDCXX
| Single Line Diagram | PZZXXXDCXX
| Electrical Control Schemes | PZZXXXDCXX
| PLC Input-Output List | TBD
| PLC Control Philosophy | TBD
| PLC Control Loop | TBD
4 | SUPPLY REQUIREMENTS
| Incoming UPS Supply | 230 VAC, 1-Phase, 2 wire
| Incoming Non-UPS Supply | 230 VAC, 1-Phase, 2 wire
| Frequency | 50 Hz +/-5%
5 | SITE DETAILS
| Project Location | Pune
| Ambient Temperature (Max) | 45 Deg.C
| Ambient Temperature (Min) | 35 Deg.C
| Electrical Design Temperature | 45 Deg.C
| Seismic Zone | 2
| Area Classification | Safe Area
6 | CONSTRUCTION
| Design Standard, Manufacturers Standdard & Testing Standard | IEC 61439
| IP Protection | IP 52
| Type of Construction for Board | Single front
| Panel Front Type | From IA (Non-Compartmental)
| Panel Mounting | Base frame
| Height of Base Frame | 100mm
| Height of Panel | 2100mm
7 | THICKNESS
| Component Mounting Plate | 2.0mm
| Door | 1.6mm
| Top & Side | 1.6mm
| Gland Plate | 3.0mm
| Gland Plate Type | Drilled - Removable
| Cable Entry Position | Top
| Earth Busbar Position | Bottom
8 | PAINTING / POWDER COATING
| Paint Shade for Interior and exterior | RAL 7032
| Paint Shade for Component Mounting Plate | RAL 2000
| Paint Shade for Base Frame | Black
| Paint Coating Thickness | 60-70 Microns (for domestic order) & 100 Microns (for Export order) / As per Client specification
| Standard for Pretreatment | - Panel Shall Be Degreased And Derusted (7 Tank Pretreatment) - Panel Shall Be Powder Coated. OR - OEM standard for pretreatment.
General Requirments For Construction
10 | PANEL WIRING
| Power wiring ( L1, L2, L3, N) | Red,Yellow,Blue,Black
| Cable Size | Min.2.5 sq.mm
| Control Wiring ( P, N, E) | Grey,Black
| Cable Size | 1 Sq.mm
| 24 VDC Wiring (+, - ) | Orange,White
| Cable Size | 0.75 Sq.mm
| Analog Signal Wiring (+, - ) | Brown,White Shielded Cable
| Cable Size | 0.5 Sq.mm
| RTD / Thermocouple Wiring (+, - ) | Brown,White Shielded Cable
| Cable Size | 0.5 Sq.mm
| Cable Insulation (PVC) | Flame Retardant Low Smoke
General Note Internal Wiring
11 | PANEL MOUNTEED
A | PANEL MOUNTED PUSH BUTTONS & COLOURS
| Emergency Stop Push button | Mushroom headed Stayput ( Key to release) Red Colour
| Electronic Hooter | Not-applicable
| Electronic Hooter acknowledge | Not Applicable
B | PANEL MOUNTED INDICATING LAMPS & COLOURS
| Panel Power Supply ON | Green
| Panel Power Supply OFF | Red
C | TERMINAL BLOCK CONNECTORS
| Power Terminal Clipon | Min.4 Sq.mm Clipon Type
| Power Terminal Busbar Type | Above 4 sq.mm Busbar Type
| DI Modules Terminal | Fuse With LED Terminal
| DO Modules Terminal | Fuse With LED Terminal
| AI Modules Terminal | Fuse Terminal
| AO Modules Terminal | Fuse Terminal
| RTD Modules Terminal | Fuse Terminal
| Thermocouple Modules Terminal | Fuse Terminal
| Spare Terminal | 10%
12 | IDENTIFICATION OF COMPONENTS
| Ferrule | Straight ferrule
| Ferrule Note | Printed Ferrules-Black Letters On White Sleeves
| Device Identification of components | PVC sticker with black letters
13 | PANELS OTHERS
| Cooling Fans | Applicable
| Louvers and Filters | Applicable
14 | SPARES
Commissioning Spare
Two Year Operational Spare
15 | UPS
| UPS Scope | Custmor scope
| UPS Input Voltage 3-Phase | Not Applicable
| UPS Input Voltage 1-Phase | Not Applicable
| UPS Output Voltage 1-Phase | 230 VAC, 1-Phase, 2 wire
| UPS Type | Not Applicable
| UPS Battery Type | Not Applicable
| UPS Battery Backup Time | Not Applicable
| UPS Battery Mounting Stand | Not Applicable
| UPS Redundancy | Not Applicable
16 | PLC
| PLC Hardware Make | Allen Bradley
PLC CPU System Series
| PLC CPU System Input Voltage | 24 VDC
PLC CPU System Memory Free Space
17 | INPUT / OUTPU MODULES
A | DI Modules
| Channel Density | 8 Nos.Per Card
| Loop Current | VTS
| Isolation | Galvanic Isolation
| Type of Input | POTENTIAL FREE CONTACTS
| Interrogation Voltage | 24 VDC
| Scan time | VTS
B | DO Modules
| Channel Density | 8 Nos.Per Card
| Loop Current | VTS
| Isolation | Galvanic Isolation
| Type of Output | POTENTIAL FREE CONTACTS
C | Interposing Relay
Interposing Relay
Interposing Relay Contacts Rating
Interposing Relay No. of Contacts
D | AI Modules
| Channel Density | 8 Nos.Per Card
| Loop Current | VTS
| Isolation | Galvanic Isolation
| Type of Input | 4-20 mA DC
| Scan Time | VTS
| HART Protocol support | Applicable
E | AO Modules
| Channel Density | 8 Nos.Per Card
| Loop Current | VTS
| Isolation | Galvanic Isolation
| Type of Output | 4-20 mA DC
| Scan Time | VTS
| HART Protocol Support | Applicable
F | RTD Modules
| Channel Density | 8 Nos.Per Card
| Loop Current | VTS
| Isolation | Galvanic Isolation
Type of Intput
| Scan Time | VTS
| HART Protocol Support | Applicable
G | Thermocopule Modules
| Channel Density | 8 Nos.Per Card
| Loop Current | VTS
| Isolation | Galvanic Isolation
Type of Intput
| Scan Time | VTS
| HART Protocol Support | Applicable
H | Universal Modules
| Channel Density | 8 Nos.Per Card
| Loop Current | VTS
| Isolation | Galvanic Isolation
Type of Intput
| Scan Time | VTS
| HART Protocol Support | Applicable
18 | SPARE INPUT / OUTPUT NOTES.
19 | HMI
| HMI Size | 12 Inch
| HMI (Quantity) | One
| HMI Hardware Make | Allen Bradley
HMI Series
| HMI Input Voltage | 24 VDC
HMI Battery Back-up
20 | HUMAN INTREFACE DEVICE
| Engineering Station | One
| Engineering Cum Operating Station | Not Applicable
| Operating Station | Not Applicable
21 | SOFTWARE LICENSE
| SCADA Runtime License | One
| SCADA Program Development License | One
| PLC Programming License Software | One
22 | REDUNDANCY
| Power Supply PLC CPU System | Applicable
| Power Supply Input-Output Module | Applicable
| PLC CPU System | Applicable
| PLC Input-Output Modules System | Applicable
| PLC CPU Systemand PLC Input-Output Modules System | Not Applicable
| PLC CPU System and HMI / SCADA | Not Applicable
| PLC CPU System and Third Party devices. | Not Applicable
23 | ENGINEERING / OPERATING SCADA STATION
| System Hardware | Commercial grade
| PC Hardware Specifications | MINIMUM CONFIGURATION = MIN. I5/LATEST PROCESSOR, MIN. 16GB RAM, MIN. 1 TB HARD DISK, MULTIMEDIA WITH DVD R/W DRIVE, KEYBOARD MOUSE SET 1 NO'S WITH 4 USB PORT.
| Monitor Size | 32 Inch
| Windows Operating System , Microsoft Office, Anti Virus (3 year) license | WINDOWS LATEST VERSION - VTS
| Communication Cable & Hardware Between PLC CPU System & SCADA PC | APPROX. 50 METER PER PC
| Printer with Suitable Communication cable | Applicable
| Printer Type | Laser printer
| Printer Type | A4
| Printer - Qty. | One
| Furniture ( wooden Table with Chair) | Applicable
| Console with Chair | Applicable
| PLC logic Diagram with Tag No. / Rung No & it’s Descriptions. | Applicable
| Loop Drawing for Complete Project | Applicable
24 | COMMUNICATION
| All Interface Signals and Control logic shall be Implemented. | Not Applicable
| Signal from Differential Pressure flow Transmitters shall be linearized. | Not Applicable
A | PLC CPU System with Third Party Communication Protocol | Modbus
| Third Party Communication Protocol | 1) IIOT Gateway - Ethernet communication 2) Boiler MCC Remote IO Section - Ethernet communication (Note : MCC Panel Internal Communication to Remote IO Section - - Panel Incomer communication to Remote IO PLC Section - Ethernet - MFM communication to Remote IO PLC Section - Ethernet - VFD communication to Remote IO PLC Section - Ethernet - Feeder IO - Refer Remote IO List. Note - MFM, VFD, ACB Incomer - Address List & Parameter shall be configure by PLC Vendor for Status indications
| Communication Cable & Hardware Between PLC CPU System & Third Party | APPROX. 50 METER
B | PLC CPU System With Client System communication | Not Applicable
| Client System communication | Applicable (Redundant Communication ports to Fiber Optic Gateway for Communication to customer DCS. Note: Ethernet IP is preferrable protocol for communication of above package.
| Communication Cable & hardware Between PLC CPU System & Client System | APPROX. 50 METER
C | IIOT | Not Applicable
| IIOT gate way is mounted in PLC panel | IIOT gate way is mounted in PLC panel. Vendor to make the necessary mounting provision for the same. (Details will be shared during detailing). IIOT is in Thermax SSBU Scope of supply. IIOT will be installed at Site. IIOT is suitable for Profinet/Ethernet communication for which PLC vendor to ensure the compatability with Supplied PLC's.
| IIOT gate way Note | 1) IIOT Gateway - Ethernet communication 2) Boiler MCC Remote IO Section - Ethernet communication (Note : MCC Panel Internal Communication to Remote IO Section - - Panel Incomer communication to Remote IO PLC Section - Ethernet - MFM communication to Remote IO PLC Section - Ethernet - VFD communication to Remote IO PLC Section - Ethernet - Feeder IO - Refer Remote IO List. Note - MFM, VFD, ACB Incomer - Address List & Parameter shall be configure by PLC Vendor for Status indications
D | BURNER CONTROLLER LMV | Not Applicable
| Burner Controller LMV is mounted in PLC panel | Burner Controller LMV in PLC panel. Vendor to make the necessary mounting provision for the same. (Details will be shared during detailing). Burner Controller LMV is in Thermax Scope of supply. Burner Controller LMV is suitable for Profinet/Ethernet communication for which PLC vendor to ensure the compatability with Supplied PLC's.
| Communication Cable & hardware Between PLC CPU System & Burner Controller LMV | APPROX. 50 METER
Burner Controller LMV Note
25 | PROJECT SPECIFIC NOTES
26 | GENERAL INSTRUCTION & NOTES.
1 | Non-UPS power supply shall be use for all panel utilities.
CPU, Power supply, HMI/SCADA, Field devices,Fan/tubelight etc. shall be provided with 2 pole MCB isolation.
Power supply positive voltage shall be connected through isolation (MCB/TB with LEB) & negative shall be connected directly to complete loop.
DCS will be master & PLC will be slave in configuration.
As built Document set rquired with rev no. date & same shall be submit to TL engineering after FAT.
PLC panel vendor will be responsible for all modification required at site with confirmation from TL .
PLC Vendor to submit to applicable As built drawings & Documents to TL.
PLC Vendor to support during Pre-Commissioning & Commissioning as per the requrements without any time & Commercial to TL
PBDDC00526- FDS shall be followed by PLC panel vendor- (Header may update as per SCADA software revision).
Terminal size shall be 1 size higher than wire size subjected to a minimum of 2.5 mm2. Terminas shall be segregated accordingly to voltage levels.
Care shall be taken to separate signal, control, RTD, TC and power supply cables providing separate ducts, terminal strips/ blocks etc. Additional terminals shall be provided for looping if necessary. Short links for looping shall be provided wherever required.
Terminal housing shall be sized with due consideration to accessibility and maintenance.
100-mm minimum space shall be provided between terminal strips and sides of the duct/panel parallel to the strip for up to 50 terminals and an additional 25 mm for each additional 25 terminals.
100mm minimum space to be provided between two terminal strips for up to 50 terminal and an additional 35 mm for each 25 additional terminals.
100mm minimum space shall be provided between terminal strip and top or bottom of the duct/panel for up to 50 terminals and an additional 25 mm for each additional 25 terminal.
The bottom of any termnal strips shall not be lower than 300mm from the gland plate.
All terminal strips shall be mounted on suitable anodized metallic DIN rail.
Removable acralic protection cover shall be provided for all power circuit / terminals.
Vendor to fullfill or comply all safety / operational requirements.
28 | Applicable Deliverables
1 | PLC system Architecture
Panel GA Drawing
Panel Wiring Drawing
Panel Input/Output Mappning List
Loop Drawing
Heat load and Cooling Calculation
Power Supply Load List
UPS sizing calculation
Test Certificates ( Short Circuit, IP Protection,etc)
29 | DOCUMENTATION:
1 | Following documentation (with respective native files) shall be supplied by PLC vendor as a minimum:
PLC system Architecture.
PLC GAD – internall & External both.
PLC Power wiring diagram.
PLC Control & Signal wiring diagram.
IO mapping list.
Compliance to Project QAP.
Heat load of the PLC and complete system.
Power supply calculations.
Startup operations for PLC.
Detailed installation, maintenance and operation manuals of each equipment / component.
Any other HARDWARE / INFORMATION / DOCUMENTATION as required by CUSTOMER / Thermax Ltd. shall be provided by PLC vendor.
All the above documents may require corrections during various stages of contract execution, vendor shall comply the same without any delay & commercial implications to Thermax Ltd.
30 | SPECIFIC NOTES FOR OEM:
1 | All the item makes shall be as per the project approved vendor list.
Any of the comment been incorporated in datasheet shall be highlighted / indicated with revision markings. Any such revision without revision marking shall not be considered valid for review or approval.
Vendor to confirm compliance to this specification as his offer, if there is any deviation against the specifications same shall be listed for Thermax Ltd. approval during pre-order stage.
Any deviation against this specification shall be listed in a separate editable Thermax Ltd. format (in Excel) to maintain the record of conclusions, comments made during pre-order stage.
Vendor will be fully responsible for any change in technical specification which is been made without highlighting / notifying to Thermax Ltd.
Vendor to ask for the specific details if any required from Thermax Ltd., no assumption on the inputs from Thermax Ltd. shall be made by Vendor.
Vendors need to support for documentation till Approval, As built, Hand over to Customer without any time & commercial impact to Thermax Ltd.
Vendor to mention “Thermax Ltd. project number / Name / Part Number/ Tag Number / document – specification Number” on each of their drawing / documents.
Vendor to comply project QRS 100% in pre-order stage OR shall seek Thermax Ltd. QAC/QAP clearance/ approval on the deviations.
All Tag plates shall be an engraved on stainless-steel plate attached to the instrument by SS 316 screws or pins.
31 | Certified Plate specification:
1 | As a minimum the following information shall be provided:
Type of Approval & mark of certifying body
Certifying Authority name.
Certificate number & date.
Area classification, gas group, temperature rating (zone /group / class).
Supplier model / type number
Supplier serial number.