## COVER
THERMAX LIMITED
HEATING
PUNE — 411 019
| TITLE |  | LOCAL ISOLATOR SPECIFICATION AND LIST
CLIENT
CONSULTANT
PROJECT
THERMAX O.C. NO.
THERMAX DOC. NO. / CLIENT DOC. NO.
| R0 |  | ISSUED FOR APPROVAL
| REV NO. | DATE | DESCRIPTION | PREPD. BY | CHKD. BY | APPD. BY | 5.5

## ISOLATOR
FIELD MOTOR ISOLATOR GENERAL SPECIFICATIONS
| Specifications | Isolator for Safe Area | Isolator for Hazardous Area
1 | Type
2 | IP Protection
3 | Enclosure MOC & Thickness
4 | Quantity
5 | Isolator Colour Shade
6 | Cable Entry, Gland Plate Thickness
7 | Canopy
8 | Canopy Type
Specifications:
1 | Isolator rating to be confirmed by Panel vendor/Isolator vendor.
2 | Isolator shall be provided with LOTO / Padlock arrangement .
3 | Field Isolator potential free ON feedback through Auxiliary Contact shall be available.
4 | Isolator box shall have cable entry And Gland Size As per Isolator BOM Sheet. Power Cable IN & OUT (Gland Size & Cable Entry) Isolator feedback (Gland Size & Cable Entry)
5 | All components shall be mounted on hinged, gasketed and lockable doors.
6 | All components shall be wired upto minimum 4 mm2 terminals with extra flexible wires.
7 | Inscription plates shall be in English and should be corrosion resistant type.
8 | 20% spare capacity shall be provided on the terminal blocks.
9 | Isolator shall be supplied with necessary GI mounting hardware.
10 | ISOLATOR shall be provided with two Earthing Brass Bolt / Nut Provided on side. Internal door & body Earthing through copper yellow green insulated cable.
11 | Cable Gland Excluded From Vendor scope of supply.
12 | Tag Plates for each ISOLATOR Shall be of MOC traffolyte engraved with black letters on white background.
13 | Letters on Black Background. The Letter size shall be 6 mm.
14 | Note : Certification & Documents 1. GA Drawing, Front, Elevations, cross sectional, Component & Fixing details for Engineering Approval. 2. Routine Test Certificate. 3. Ingress Protection Certification. 4. Model No. Details.
Make of Components:
1 | All components shall be As per approved vendor list

## ISOLATOR LIST SAFE AREA
ISOLATOR BOM LIST FOR SAFE AREA
SR.NO. | TAG. NO. | DESCRIPTION | kW RATING | ISOLATOR RATING ( Amp ) | CANOPY REQUIRED | MOTOR LOCATION | GLAND SIZE | PART CODE | REMARK
1 | M-01 | PUMP-1 | 3.7 |  |  |  | 2 No X 1 "ET 1No X 3/4 "ET
2 | M-02 | PUMP-2 | 3.7
3 | M-03 | PUMP-3 | 2.2
4 | M-04 | PUMP-4 | 2.2
5 | M-05 | PUMP-5 | 2.2
6 | M-06 | PUMP-6 | 2.2
7 | M-07 | PUMP-7 | 2.2
8 | M-08 | PUMP-8 | 2.2
9 | M-09 | PUMP-9 | 1.5
10 | M-10 | PUMP-10 | 1.5
11 | M-11 | PUMP-11 | 18.5
12 | M-12 | PUMP-12 | 18.5
13 | M-13 | PUMP-13 | 18.5
14 | M-14 | PUMP-14 | 3.7
15 | M-15 | PUMP-15 | 3.7
16 | M-16 | PUMP-16 | 2.2
|  | Total Quantity |  | Nos

## ISOLATOR LIST HAZARDOUS AREA
ISOLATOR BOM LIST FOR HAZARDOUS AREA
SR.NO. | TAG. NO. | DESCRIPTION | kW RATING | ISOLATOR RATING ( Amp ) | CANOPY REQUIRED | ZONE | GAS GROUP | TEMPARETURE CLASS | MOTOR LOCATION | GLAND SIZE | PART CODE | REMARK
1 | M-01 | PUMP-1 | 3.7
2 | M-02 | PUMP-2 | 3.7
3 | M-03 | PUMP-3 | 2.2
4 | M-04 | PUMP-4 | 2.2
5 | M-05 | PUMP-5 | 2.2
6 | M-06 | PUMP-6 | 2.2
7 | M-07 | PUMP-7 | 2.2
8 | M-08 | PUMP-8 | 2.2
9 | M-09 | PUMP-9 | 1.5
10 | M-10 | PUMP-10 | 1.5
11 | M-11 | PUMP-11 | 18.5
12 | M-12 | PUMP-12 | 18.5
13 | M-13 | PUMP-13 | 18.5
14 | M-14 | PUMP-14 | 3.7
15 | M-15 | PUMP-15 | 3.7
16 | M-16 | PUMP-16 | 2.2
|  | Total Quantity |  | Nos