## BRASS (hidden)
[16 empty] | YES | COMET | Ni PLATED BRASS
Sr.No | MAKE | CAT.NO |  | ENTRY THREAD | CABLE OD |  |  |  |  | HOLE | CABLE OD | MAKE | GLAND CAT NO | ENTRY THREAD |  | NO | BRACO | SS304
| Make | Cat. No |  | Nipple Thread Inch | above | upto |  |  |  | 0.75 " | 8 | COMET | FALSE | Nipple Thread Inch
1 | BRACO | BPW 3/8 | ARMOURED | 0.625" ET | 8 | 12 |  |  |  | 0.75 " | 8 | COMET | FALSE | 0.625" ET
2 | BRACO | BPW 1/2" | ARMOURED | 0.625" ET | 8 | 13.5 | [7 empty] | 0.75" ET
3 | BRACO | BPW-001S | ARMOURED | 0.75" ET | 8 | 13.5 | [7 empty] | 1" ET
4 | BRACO | BPW 5/8" | ARMOURED | 0.75" ET | 11 | 15 | [7 empty] | 1.25" ET
5 | BRACO | BPW 001 | ARMOURED | 0.75" ET | 12.5 | 16 | [7 empty] | 1.5" ET
6 | BRACO | BPW-01S | ARMOURED | 0.75" ET | 13 | 16.5 | [7 empty] | 2" ET
7 | BRACO | BPW 01 | ARMOURED | 0.75" ET | 15 | 18 | [7 empty] | 2.5" ET
8 | BRACO | BPW 01L | ARMOURED | 1" ET | 15 | 18 | [7 empty] | 3" ET
9 | BRACO | BPW 02 | ARMOURED | 1" ET | 18 | 20 | [7 empty] | 3.25" ET
10 | BRACO | BPW 02S | ARMOURED | 0.75" ET | 18 | 20 | [7 empty] | 3.5" ET
11 | BRACO | BPW 03 | ARMOURED | 1" ET | 20 | 23 | [7 empty] | 4" ET
12 | BRACO | BPW 1" | ARMOURED | 1" ET | 20 | 23 | [7 empty] | 4.5" ET
13 | BRACO | BPW 04 | ARMOURED | 1" ET | 23 | 26 | [7 empty] | 40 MM
14 | BRACO | BPW 04L | ARMOURED | 1.25" ET | 23 | 26 | [7 empty] | 42 MM
15 | BRACO | BPW 05 | ARMOURED | 1.25" ET | 26 | 30 | [7 empty] | 70 MM
16 | BRACO | BPW 05L | ARMOURED | 1.5" ET | 26 | 30 | [7 empty] | 3.75" ET | 3.75" ET
17 | BRACO | BPW 06 | ARMOURED | 1.5" ET | 30 | 33 | [7 empty] | M28
18 | BRACO | BPW 06S | ARMOURED | 1.25" ET | 30 | 33 | [7 empty] | M40
19 | BRACO | BPW 07 | ARMOURED | 1.5" ET | 33 | 37 | [7 empty] | M42
20 | BRACO | BPW 08 | ARMOURED | 2" ET | 37 | 41 | [7 empty] | M70
21 | BRACO | BPW 09 | ARMOURED | 2" ET | 41 | 46 | [7 empty] | M16
22 | BRACO | BPW 010 | ARMOURED | 2" ET | 46 | 52 | [7 empty] | M20
23 | BRACO | BPW-010L | ARMOURED | 2.5" ET | 46 | 52 | [7 empty] | M25
24 | BRACO | BPW 011 | ARMOURED | 2.5" ET | 52 | 60 | [7 empty] | M32
25 | BRACO | BPW 012 | ARMOURED | 3" ET | 60 | 66 | [7 empty] | M50
26 | BRACO | BPW 013S | ARMOURED | 3" ET | 66 | 72 | [7 empty] | M63
27 | BRACO | BPW 013 | ARMOURED | 3.25" ET | 72 | 78 | [7 empty] | M75
28 | BRACO | BPW 014 | ARMOURED | 3.5" ET | 78 | 83 | [7 empty] | M82
29 | BRACO | BPW 015 | ARMOURED | 4" ET | 83 | 93 | [7 empty] | M90
30 | BRACO | BPW 016 | ARMOURED | 4.5" ET | 93 | 104 | [7 empty] | M100
31 | COMET | CBW01SS | ARMOURED | 0.75" ET | 8 | 13 | [7 empty] | M115
32 | COMET | CBW01S | ARMOURED | 0.75" ET | 13.5 | 16 | [7 empty] | 1/2" NPT
33 | COMET | CBW01 | ARMOURED | 0.75" ET | 16.5 | 18 | [7 empty] | 3/4" NPT
34 | COMET | CBW01A | ARMOURED | 1" ET | 16.5 | 18 | [7 empty] | 1" NPT
35 | COMET | CBW02 | ARMOURED | 1" ET | 18.5 | 20 | [7 empty] | 1.25" NPT
36 | COMET | CBW02A | ARMOURED | 0.75" ET | 18.5 | 20 | [7 empty] | 1.5" NPT
37 | COMET | CBW03 | ARMOURED | 1" ET | 20.5 | 23 | [7 empty] | 2" NPT
38 | COMET | CBW04 | ARMOURED | 1" ET | 23.5 | 26 | [7 empty] | 2.5" NPT
39 | COMET | CBW04A | ARMOURED | 1.25" ET | 23.5 | 26 | [7 empty] | 3" NPT
40 | COMET | CBW05 | ARMOURED | 1.25" ET | 26.5 | 30 | [7 empty] | 3.5" NPT
41 | COMET | CBW05A | ARMOURED | 1.5" ET | 26.5 | 30
42 | COMET | CBW06 | ARMOURED | 1.5" ET | 30.5 | 33
43 | COMET | CBW06A | ARMOURED | 1.25" ET | 30.5 | 33
44 | COMET | CBW07 | ARMOURED | 1.5" ET | 33.5 | 37
45 | COMET | CBW08 | ARMOURED | 2" ET | 37.5 | 41
46 | COMET | CBW09 | ARMOURED | 2" ET | 41.5 | 46
47 | COMET | CBW010 | ARMOURED | 2" ET | 46.5 | 52
48 | COMET | CBW10A | ARMOURED | 2.5" ET | 46.5 | 52
49 | COMET | CBW011S | ARMOURED | 2.5" ET | 52.5 | 56
50 | COMET | CBW011 | ARMOURED | 2.5" ET | 56.5 | 60
51 | COMET | CBW012 | ARMOURED | 3" ET | 60.5 | 66
52 | COMET | CBW013A | ARMOURED | 3" ET | 66.5 | 72
53 | COMET | CBW013 | ARMOURED | 3.25" ET | 72.5 | 78
54 | COMET | CBW014 | ARMOURED | 3.5" ET | 78.5 | 84
55 | COMET | CBW015 | ARMOURED | 4" ET | 84.5 | 92
56 | COMET | CBW016 | ARMOURED | 4.5" ET | 92.5 | 104
57 | BRACO | BPT-001SS | UNARMOURED | 0.75" ET | 5 | 10
58 | BRACO | BPT-001S | UNARMOURED | 0.75" ET | 10 | 13.5
59 | BRACO | BPT-001 | UNARMOURED | 0.75" ET | 11 | 14.5
60 | BRACO | BPT-01 L | UNARMOURED | 1" ET | 14 | 18
61 | BRACO | BPT-02 | UNARMOURED | 1" ET | 18 | 20
62 | BRACO | BPT-03 SP | UNARMOURED | 1.25" ET | 20 | 23
63 | BRACO | BPT-04L | UNARMOURED | 1.25" ET | 23 | 26
64 | BRACO | BPT-05 L | UNARMOURED | 1.5" ET | 26 | 30
65 | BRACO | BPT-06 SP | UNARMOURED | 40 MM | 30 | 33 | 1.57 "
66 | BRACO | BPT-07 SP | UNARMOURED | 42 MM | 33 | 36 | 1.65 "
67 | BRACO | BPT-08 | UNARMOURED | 2" ET | 36 | 41
68 | BRACO | BPT-09 | UNARMOURED | 2" ET | 41 | 44
69 | BRACO | BPT-010L | UNARMOURED | 2.5" ET | 44 | 52
70 | BRACO | BPT-011S | UNARMOURED | 2.5" ET | 52 | 55
71 | BRACO | BPT-011L | UNARMOURED | 70 MM | 55 | 60 | 2.75 "
72 | BRACO | BPT-012 | UNARMOURED | 3" ET | 60 | 66
73 | BRACO | BPT-013SL | UNARMOURED | 3.25" ET | 66 | 72
74 | BRACO | BPT-013 | UNARMOURED | 3.5" ET | 72 | 78
75 | BRACO | BPT-014 | UNARMOURED | 3.75" ET | 78 | 83
76 | BRACO | BPT-015 | UNARMOURED | 4" ET | 83 | 93
77 | BRACO | BPT-016 | UNARMOURED | 4.5" ET | 93 | 104
78 | COMET | CBW01SS | UNARMOURED | 0.75" ET | 5 | 13
79 | COMET | CBW01S | UNARMOURED | 0.75" ET | 13.5 | 14.5
80 | COMET | CBW01A | UNARMOURED | 1" ET | 14.5 | 18
81 | COMET | CBW02 | UNARMOURED | 1" ET | 18.5 | 20
82 | COMET | CBW03SP | UNARMOURED | M28 | 20.5 | 22
83 | COMET | CBW04A | UNARMOURED | 1.25" ET | 22.5 | 26
84 | COMET | CBW05A | UNARMOURED | 1.5" ET | 26.5 | 30
85 | COMET | CBW06SP | UNARMOURED | M40 | 30.5 | 33
86 | COMET | CBW07SP | UNARMOURED | M42 | 33.5 | 36
87 | COMET | CBW08 | UNARMOURED | 2" ET | 36.5 | 41
88 | COMET | CBW09 | UNARMOURED | 2" ET | 41.5 | 44
89 | COMET | CBW010A | UNARMOURED | 2.5" ET | 44.5 | 52
90 | COMET | CBW011SP | UNARMOURED | M70 | 52.5 | 60
91 | COMET | CBW012 | UNARMOURED | 3" ET | 60.5 | 66
92 | COMET | CBW013 | UNARMOURED | 3.25" ET | 66.5 | 75
93 | COMET | CBW014 | UNARMOURED | 3.5" ET | 75.5 | 80
94 | COMET | CBW015 | UNARMOURED | 4" ET | 81 | 88
95 | BRACO | BPW 3/8 WITH M16 THREADING | ARMOURED | M16 | 8 | 12 |  |  | BPW 3/8
96 | BRACO | BPW 1/2" WITH M16 THREADING | ARMOURED | M16 | 8 | 13 |  |  | BPW 1/2"
97 | BRACO | BPW-001S WITH M20 THREADING | ARMOURED | M20 | 8 | 12.5 |  |  | BPW-001S
98 | BRACO | BPW 5/8" WITH M20 THREADING | ARMOURED | M20 | 11 | 15 |  |  | BPW 5/8"
99 | BRACO | BPW 001 WITH M20 THREADING | ARMOURED | M20 | 12.5 | 16 |  |  | BPW 001
100 | BRACO | BPW-01S WITH M20 THREADING | ARMOURED | M20 | 13 | 16.5 |  |  | BPW-01S
101 | BRACO | BPW 01 WITH M20 THREADING | ARMOURED | M20 | 15 | 18 |  |  | BPW 01
102 | BRACO | BPW 01L WITH M25 THREADING | ARMOURED | M25 | 15 | 18 |  |  | BPW 01L
103 | BRACO | BPW 02 WITH M25 THREADING | ARMOURED | M25 | 18 | 20 |  |  | BPW 02
104 | BRACO | BPW 02S WITH M20 THREADING | ARMOURED | M20 | 18 | 20 |  |  | BPW 02S
105 | BRACO | BPW 03 WITH M25 THREADING | ARMOURED | M25 | 20 | 23 |  |  | BPW 03
106 | BRACO | BPW 1" WITH M25 THREADING | ARMOURED | M25 | 20 | 23 |  |  | BPW 1"
107 | BRACO | BPW 04 WITH M25 THREADING | ARMOURED | M25 | 23 | 26 |  |  | BPW 04
108 | BRACO | BPW 04L WITH M32 THREADING | ARMOURED | M32 | 23 | 26 |  |  | BPW 04L
109 | BRACO | BPW 05 WITH M32 THREADING | ARMOURED | M32 | 26 | 30 |  |  | BPW 05
110 | BRACO | BPW 05L WITH M40 THREADING | ARMOURED | M40 | 26 | 30 |  |  | BPW 05L
111 | BRACO | BPW 06 WITH M40 THREADING | ARMOURED | M40 | 30 | 33 |  |  | BPW 06
112 | BRACO | BPW 06S WITH M32 THREADING | ARMOURED | M32 | 30 | 33 |  |  | BPW 06S
113 | BRACO | BPW 07 WITH M40 THREADING | ARMOURED | M40 | 33 | 37 |  |  | BPW 07
114 | BRACO | BPW 08 WITH M50 THREADING | ARMOURED | M50 | 37 | 41 |  |  | BPW 08
115 | BRACO | BPW 09 WITH M50 THREADING | ARMOURED | M50 | 41 | 46 |  |  | BPW 09
116 | BRACO | BPW 010 WITH M50 THREADING | ARMOURED | M50 | 46 | 52 |  |  | BPW 010
117 | BRACO | BPW-010L WITH M63 THREADING | ARMOURED | M63 | 46 | 52 |  |  | BPW-010L
118 | BRACO | BPW 011 WITH M63 THREADING | ARMOURED | M63 | 52 | 60 |  |  | BPW 011
119 | BRACO | BPW 012 WITH M75 THREADING | ARMOURED | M75 | 60 | 66 |  |  | BPW 012
120 | BRACO | BPW 013S WITH M75 THREADING | ARMOURED | M75 | 66 | 72 |  |  | BPW 013S
121 | BRACO | BPW 013 WITH M82 THREADING | ARMOURED | M82 | 72 | 78 |  |  | BPW 013
122 | BRACO | BPW 014 WITH M90 THREADING | ARMOURED | M90 | 78 | 83 |  |  | BPW 014
123 | BRACO | BPW 015 WITH M100 THREADING | ARMOURED | M100 | 83 | 93 |  |  | BPW 015
124 | BRACO | BPW 016 WITH M115 THREADING | ARMOURED | M115 | 93 | 104 |  |  | BPW 016
125 | COMET | CBW01SS WITH M16 THREADING | ARMOURED | M16 | 8 | 13 |  |  | CBW01SS | WITH | M16 | THREADING
126 | COMET | CBW01SS WITH M20 THREADING | ARMOURED | M20 | 8 | 13 |  |  | CBW01SS | WITH | M20 | THREADING
127 | COMET | CBW01SS WITH M25 THREADING | ARMOURED | M25 | 8 | 13 |  |  | CBW01SS | WITH | M25 | THREADING
128 | COMET | CBW01S WITH M16 THREADING | ARMOURED | M16 | 13.5 | 16 |  |  | CBW01S | WITH | M16 | THREADING
129 | COMET | CBW01S WITH M20 THREADING | ARMOURED | M20 | 13.5 | 16 |  |  | CBW01S | WITH | M20 | THREADING
130 | COMET | CBW01S WITH M25 THREADING | ARMOURED | M25 | 13.5 | 16 |  |  | CBW01S | WITH | M25 | THREADING
131 | COMET | CBW01 WITH M20 THREADING | ARMOURED | M20 | 16.5 | 18 |  |  | CBW01 | WITH | M20 | THREADING
132 | COMET | CBW01 WITH M25 THREADING | ARMOURED | M25 | 16.5 | 18 |  |  | CBW01 | WITH | M25 | THREADING
133 | COMET | CBW02 WITH M20 THREADING | ARMOURED | M20 | 18.5 | 20 |  |  | CBW02 | WITH | M20 | THREADING
134 | COMET | CBW02 WITH M25 THREADING | ARMOURED | M25 | 18.5 | 20 |  |  | CBW02 | WITH | M25 | THREADING
135 | COMET | CBW03 WITH M25 THREADING | ARMOURED | M25 | 20.5 | 23 |  |  | CBW03 | WITH | M25 | THREADING
136 | COMET | CBW04 WITH M25 THREADING | ARMOURED | M25 | 23.5 | 26 |  |  | CBW04 | WITH | M25 | THREADING
137 | COMET | CBW04 WITH M32 THREADING | ARMOURED | M32 | 23.5 | 26 |  |  | CBW04 | WITH | M32 | THREADING
138 | COMET | CBW05 WITH M32 THREADING | ARMOURED | M32 | 26.5 | 30 |  |  | CBW05 | WITH | M32 | THREADING
139 | COMET | CBW05 WITH M40 THREADING | ARMOURED | M40 | 26.5 | 30 |  |  | CBW05 | WITH | M40 | THREADING
140 | COMET | CBW06 WITH M32 THREADING | ARMOURED | M32 | 30.5 | 33 |  |  | CBW06 | WITH | M32 | THREADING
141 | COMET | CBW06 WITH M40 THREADING | ARMOURED | M40 | 30.5 | 33 |  |  | CBW06 | WITH | M40 | THREADING
142 | COMET | CBW07 WITH M40 THREADING | ARMOURED | M40 | 33.5 | 37 |  |  | CBW07 | WITH | M40 | THREADING
143 | COMET | CBW08 WITH M50 THREADING | ARMOURED | M50 | 37.5 | 41 |  |  | CBW08 | WITH | M50 | THREADING
144 | COMET | CBW09 WITH M50 THREADING | ARMOURED | M50 | 41.5 | 46 |  |  | CBW09 | WITH | M50 | THREADING
145 | COMET | CBW010 WITH M50 THREADING | ARMOURED | M50 | 46.5 | 52 |  |  | CBW010 | WITH | M50 | THREADING
146 | COMET | CBW010 WITH M63 THREADING | ARMOURED | M63 | 46.5 | 52 |  |  | CBW010 | WITH | M63 | THREADING
147 | COMET | CBW011 WITH M63 THREADING | ARMOURED | M63 | 52.5 | 60 |  |  | CBW011 | WITH | M63 | THREADING
148 | COMET | CBW012 WITH M75 THREADING | ARMOURED | M75 | 60.5 | 66 |  |  | CBW012 | WITH | M75 | THREADING
149 | COMET | CBW013 WITH M82 THREADING | ARMOURED | M82 | 72.5 | 78 |  |  | CBW013 | WITH | M82 | THREADING
150 | COMET | CBW014 WITH M90 THREADING | ARMOURED | M90 | 78.5 | 84 |  |  | CBW014 | WITH | M90 | THREADING
| BRACO | BPW 001S-1/2 " NPT | ARMOURED | 1/2" NPT | 0 | 12.5
151 | BRACO | BPW 001-1/2 " NPT | ARMOURED | 1/2" NPT | 12.5 | 16.5
152 | BRACO | BPW-01S-1/2 " NPT | ARMOURED | 1/2" NPT | 12.5 | 17
153 | BRACO | BPW 01-1/2 " NPT | ARMOURED | 1/2" NPT | 15 | 18
154 | BRACO | BPW 02-1/2 " NPT | ARMOURED | 1/2" NPT | 18 | 20
155 | BRACO | BPW 03-1/2 " NPT | ARMOURED | 1/2" NPT | 20 | 23
156 | BRACO | BPW 01-3/4 " NPT | ARMOURED | 3/4" NPT | 15 | 18
157 | BRACO | BPW 02-3/4 " NPT | ARMOURED | 3/4" NPT | 18 | 20
158 | BRACO | BPW 03-3/4 " NPT | ARMOURED | 3/4" NPT | 20 | 23
159 | BRACO | BPW 04-3/4 " NPT | ARMOURED | 3/4" NPT | 23 | 26
160 | BRACO | BPW 04-1 " NPT | ARMOURED | 1" NPT | 23 | 26
161 | BRACO | BPW 05-1 " NPT | ARMOURED | 1" NPT | 26 | 30
162 | BRACO | BPW 06-1 " NPT | ARMOURED | 1" NPT | 30 | 33
163 | COMET | CBW01SS WITH 1/2 " NPT (M) | ARMOURED | 1/2" NPT | 8 | 13 |  | CBW01SS
164 | COMET | CBW01SS WITH 3/4 " NPT (M) | ARMOURED | 3/4" NPT | 8 | 13 |  | CBW01SS
165 | COMET | CBW01S WITH 1/2 " NPT (M) | ARMOURED | 1/2" NPT | 13.5 | 16 |  | CBW01S
166 | COMET | CBW01S WITH 3/4 " NPT (M) | ARMOURED | 3/4" NPT | 13.5 | 16 |  | CBW01S
167 | COMET | CBW01 WITH 1/2 " NPT (M) | ARMOURED | 1/2" NPT | 16.5 | 18 |  | CBW01
168 | COMET | CBW01 WITH 3/4 " NPT (M) | ARMOURED | 3/4" NPT | 16.5 | 18 |  | CBW01
169 | COMET | CBW02 WITH 3/4 " NPT (M) | ARMOURED | 3/4" NPT | 18.5 | 20 |  | CBW02
170 | COMET | CBW02 WITH 1 " NPT (M) | ARMOURED | 1" NPT | 18.5 | 20 |  | CBW02
171 | COMET | CBW03 WITH 3/4 " NPT (M) | ARMOURED | 3/4" NPT | 20.5 | 23 |  | CBW03
172 | COMET | CBW03 WITH 1 " NPT (M) | ARMOURED | 1" NPT | 20.5 | 23 |  | CBW03
173 | COMET | CBW04 WITH 1 " NPT (M) | ARMOURED | 1" NPT | 23.5 | 26 |  | CBW04
174 | COMET | CBW04 WITH 1.25 " NPT (M) | ARMOURED | 1.25" NPT | 23.5 | 26 |  | CBW04
175 | COMET | CBW05 WITH 1 " NPT (M) | ARMOURED | 1" NPT | 26.5 | 30 |  | CBW05
176 | COMET | CBW05 WITH 1.25 " NPT (M) | ARMOURED | 1.25" NPT | 26.5 | 30 |  | CBW05
177 | COMET | CBW06 WITH 1.25 " NPT (M) | ARMOURED | 1.25" NPT | 30.5 | 33 |  | CBW06
178 | COMET | CBW06 WITH 1.5 " NPT (M) | ARMOURED | 1.5" NPT | 30.5 | 33 |  | CBW06
179 | COMET | CBW07 WITH 1.25 " NPT (M) | ARMOURED | 1.25" NPT | 33.5 | 37 |  | CBW07
180 | COMET | CBW07 WITH 1.5 " NPT (M) | ARMOURED | 1.5" NPT | 33.5 | 37 |  | CBW07
181 | COMET | CBW08 WITH 1.5 " NPT (M) | ARMOURED | 1.5" NPT | 37.5 | 41 |  | CBW08
182 | COMET | CBW08 WITH 2 " NPT (M) | ARMOURED | 2" NPT | 37.5 | 41 |  | CBW08
183 | COMET | CBW09 WITH 1.5 " NPT (M) | ARMOURED | 1.5" NPT | 41.5 | 46 |  | CBW09
184 | COMET | CBW09 WITH 2 " NPT (M) | ARMOURED | 2" NPT | 41.5 | 46 |  | CBW09
185 | COMET | CBW010 WITH 2 " NPT (M) | ARMOURED | 2" NPT | 46.5 | 52 |  | CBW010
186 | COMET | CBW010 WITH 2.5 " NPT (M) | ARMOURED | 2.5" NPT | 46.5 | 52 |  | CBW010
187 | COMET | CBW011 WITH 2 " NPT (M) | ARMOURED | 2" NPT | 52.5 | 60 |  | CBW011
188 | COMET | CBW011 WITH 2.5 " NPT (M) | ARMOURED | 2.5" NPT | 52.5 | 60 |  | CBW011
189 | COMET | CBW012 WITH 2.5 " NPT (M) | ARMOURED | 2.5" NPT | 60.5 | 66 |  | CBW012
190 | COMET | CBW012 WITH 3 " NPT (M) | ARMOURED | 3" NPT | 60.5 | 66 |  | CBW012
191 | COMET | CBW013 WITH 3 " NPT (M) | ARMOURED | 3" NPT | 72.5 | 78 |  | CBW013
192 | COMET | CBW013 WITH 3.5 " NPT (M) | ARMOURED | 3.5" NPT | 72.5 | 78 |  | CBW013

## SS (hidden)
Sr.No | MAKE | CAT.NO |  | ENTRY THREAD | CABLE OD |  | HOLE | CABLE OD | MAKE | GLAND CAT NO | ENTRY THREAD
| Make | Cat. No |  | Nipple Thread Inch | above | upto | 0.75 " | 8 | COMET | FALSE | Nipple Thread Inch
1 | BRACO | SSW 1/2" | ARMOURED | 0.625" ET | 8 | 13 | 0.75 " | 8 | COMET | FALSE | 0.625" ET
2 | BRACO | SSW-001S | ARMOURED | 0.75" ET | 8 | 14 |  |  |  |  | 0.75" ET
3 | BRACO | SSW 001 | ARMOURED | 0.75" ET | [6 empty] | 1" ET
4 | BRACO | SSW-01S | ARMOURED | 0.75" ET | 12.5 | 16.5 |  |  |  |  | 1.25" ET
5 | BRACO | SSW 01 | ARMOURED | 0.75" ET | 15 | 18 |  |  |  |  | 1.5" ET
6 | BRACO | SSW 01L | ARMOURED | 1" ET | 15 | 18 |  |  |  |  | 2" ET
7 | BRACO | SSW 02 | ARMOURED | 1" ET | 18 | 20 |  |  |  |  | 2.5" ET
8 | BRACO | SSW 02S | ARMOURED | 0.75" ET | 18 | 20 |  |  |  |  | 3" ET
9 | BRACO | SSW 03 | ARMOURED | 1" ET | 20 | 23 |  |  |  |  | 3.25" ET
10 | BRACO | SSW 04 | ARMOURED | 1" ET | 23 | 26 |  |  |  |  | 3.5" ET
11 | BRACO | SSW 04L | ARMOURED | 1.25" ET | 23 | 26 |  |  |  |  | 4" ET
12 | BRACO | SSW 05 | ARMOURED | 1.25" ET | 26 | 30 |  |  |  |  | 4.5" ET
13 | BRACO | SSW 05L | ARMOURED | 1.5" ET | 26 | 30 |  |  |  |  | 40 MM
14 | BRACO | SSW 06 | ARMOURED | 1.5" ET | 30 | 33 |  |  |  |  | 42 MM
15 | BRACO | SSW 06S | ARMOURED | 1.25" ET | 30 | 33 |  |  |  |  | 70 MM
16 | BRACO | SSW 07 | ARMOURED | 1.5" ET | 33 | 37 |  |  |  |  | 3.75" ET | 3.75" ET
17 | BRACO | SSW 08 | ARMOURED | 2" ET | 37 | 41 |  |  |  |  | M28
18 | BRACO | SSW 09 | ARMOURED | 2" ET | 41 | 46 |  |  |  |  | M40
19 | BRACO | SSW 010 | ARMOURED | 2" ET | 46 | 52 |  |  |  |  | M42
20 | BRACO | SSW-010L | ARMOURED | 2.5" ET | 46 | 52 |  |  |  |  | M70
21 | BRACO | SSW 011 | ARMOURED | 2.5" ET | 52 | 60 |  |  |  |  | M16
22 | BRACO | SSW 012 | ARMOURED | 3" ET | 60 | 66 |  |  |  |  | M20
23 | BRACO | SSW 013S | ARMOURED | 3" ET | 66 | 72 |  |  |  |  | M25
24 | BRACO | SSW 013 | ARMOURED | 3.25" ET | 72 | 78 |  |  |  |  | M32
25 | BRACO | SSW 014 | ARMOURED | 3.5" ET | 78 | 83 |  |  |  |  | M50
26 | BRACO | SSW 015 | ARMOURED | 4" ET | 83 | 93 |  |  |  |  | M63
27 | BRACO | SSW 016 | ARMOURED | 4.5" ET | 93 | 104 |  |  |  |  | M75
28 | BRACO | SSW-3/8' WITH M16 THREADING | ARMOURED | M16 | 8 | 12 |  |  |  |  | M82
29 | BRACO | SSW-1/2" WITH M16 THREADING | ARMOURED | M16 | 8 | 13 |  |  |  |  | M90
30 | BRACO | SSW-001S WITH M20 THREADING | ARMOURED | M20 | 8 | 12.5 |  |  |  |  | M100
31 | BRACO | SSW-5/8" WITH M20 THREADING | ARMOURED | M20 | 11 | 15
32 | BRACO | SSW-001 WITH M20 THREADING | ARMOURED | M20 | 12.5 | 16.5
33 | BRACO | SSW-01S WITH M20 THREADING | ARMOURED | M20 | 12.5 | 16.5
34 | BRACO | SSW-01 WITH M20 THREADING | ARMOURED | M20 | 15 | 18
35 | BRACO | SSW-01L WITH M25 THREADING | ARMOURED | M25 | 15 | 18
36 | BRACO | SSW-02 WITH M25 THREADING | ARMOURED | M25 | 18 | 20
37 | BRACO | SSW-02S WITH M20 THREADING | ARMOURED | M20 | 18 | 20
38 | BRACO | SSW-03 WITH M25 THREADING | ARMOURED | M25 | 20 | 23
39 | BRACO | SSW-1" WITH M25 THREADING | ARMOURED | M25 | 20 | 23
40 | BRACO | SSW-04 WITH M25 THREADING | ARMOURED | M25 | 23 | 26
41 | BRACO | SSW-04L WITH M32 THREADING | ARMOURED | M32 | 23 | 26
42 | BRACO | SSW-05 WITH M32 THREADING | ARMOURED | M32 | 26 | 30
43 | BRACO | SSW-05L WITH M40 THREADING | ARMOURED | M40 | 26 | 30
44 | BRACO | SSW-06 WITH M40 THREADING | ARMOURED | M40 | 30 | 33
45 | BRACO | SSW-06S WITH M32 THREADING | ARMOURED | M32 | 30 | 33
46 | BRACO | SSW-07 WITH M40 THREADING | ARMOURED | M40 | 33 | 37
47 | BRACO | SSW-08 WITH M50 THREADING | ARMOURED | M50 | 37 | 41
48 | BRACO | SSW-09 WITH M50 THREADING | ARMOURED | M50 | 41 | 46
49 | BRACO | SSW-010 WITH M50 THREADING | ARMOURED | M50 | 46 | 52
50 | BRACO | SSW-010L WITH M63 THREADING | ARMOURED | M63 | 46 | 52
51 | BRACO | SSW-011 WITH M63 THREADING | ARMOURED | M63 | 52 | 60
52 | BRACO | SSW-012 WITH M75 THREADING | ARMOURED | M75 | 60 | 66
53 | BRACO | SSW-013S WITH M75 THREADING | ARMOURED | M75 | 66 | 72
54 | BRACO | SSW-013 WITH M82 THREADING | ARMOURED | M82 | 72 | 78
55 | BRACO | SSW-014 WITH M90 THREADING | ARMOURED | M90 | 78 | 83
56 | BRACO | SSW-015 WITH M100 THREADING | ARMOURED | M100 | 83 | 93
57 | BRACO | SSW-016 WITH M115 THREADING | ARMOURED | M115 | 93 | 104
58 | BRACO | SSW 1/2" NPT 001S | ARMOURED | 1/2" NPT | 8 | 13.5
59 | BRACO | SSW 001-1/2" NPT | ARMOURED | 1/2" NPT | 13.5 | 16.5
60 | BRACO | SSW 01-1/2" NPT | ARMOURED | 1/2" NPT | 15 | 18
61 | BRACO | SSW 02-1/2" NPT | ARMOURED | 1/2" NPT | 18 | 20
62 | BRACO | SSW 01-3/4" NPT | ARMOURED | 3/4" NPT | 15 | 18
63 | BRACO | SSW 02-3/4" NPT | ARMOURED | 3/4" NPT | 18 | 20
64 | BRACO | SSW 03-3/4" NPT | ARMOURED | 3/4" NPT | 20 | 23
65 | BRACO | SSW 04-3/4" NPT | ARMOURED | 3/4" NPT | 23 | 26
66 | BRACO | SSW 04-1" NPT | ARMOURED | 1" NPT | 23 | 26
67 | BRACO | SSW 05-1' NPT | ARMOURED | 1" NPT | 26 | 30
68 | BRACO | SSW 06-1" NPT | ARMOURED | 1" NPT | 30 | 33
69 | BRACO | SSW 06-1-1/4" NPT | ARMOURED | 1.25" NPT | 30 | 33
70 | BRACO | SSW 07-1-1/4" NPT | ARMOURED | 1.25" NPT | 33 | 37
71 | BRACO | SSW 08-1-1/2" NPT | ARMOURED | 1.5" NPT | 37 | 41
72 | BRACO | SSW 09-1-1/2" NPT | ARMOURED | 1.5" NPT | 41 | 46
73 | BRACO | SSW 010-1-1/2" NPT | ARMOURED | 1.5" NPT | 46 | 52
74 | BRACO | SSW 011-2" NPT | ARMOURED | 2" NPT | 52 | 60
75 | BRACO | SSW 012-2-1/2" NPT | ARMOURED | 2.5" NPT | 60 | 66
76 | BRACO | SSW 013-3" NPT | ARMOURED | 3" NPT | 72 | 78
77 | BRACO | SSWT-001S | UNARMOURED | 0.75" ET | 5 | 11
78 | BRACO | SSWT-001 | UNARMOURED | 0.75" ET | 11 | 14
79 | BRACO | SSWT-01 L | UNARMOURED | 1" ET | 14 | 18
80 | BRACO | SSWT-02 | UNARMOURED | 1" ET | 18 | 20
81 | BRACO | SSWT-03 SP | UNARMOURED | 28MM | 20 | 23
82 | BRACO | SSWT-04L | UNARMOURED | 1.25" ET | 23 | 26
83 | BRACO | SSWT-05 L | UNARMOURED | 1.5" ET | 26 | 30
84 | BRACO | SSWT-06 SP | UNARMOURED | 40MM | 30 | 33
85 | BRACO | SSWT-07 SP | UNARMOURED | 42MM | 33 | 36
86 | BRACO | SSWT-08 | UNARMOURED | 2" ET | 36 | 41
87 | BRACO | SSWT-09 | UNARMOURED | 2" ET | 41 | 44
88 | BRACO | SSWT-010L | UNARMOURED | 2.5" ET | 44 | 52
89 | BRACO | SSWT-011S | UNARMOURED | 2.5" ET | 52 | 55
90 | BRACO | SSWT-011 | UNARMOURED | 70MM | 52 | 60
91 | BRACO | SSWT-012 | UNARMOURED | 3" ET | 60 | 66
92 | BRACO | SSWT-013SL | UNARMOURED | 3.25" ET | 66 | 72
93 | BRACO | SSWT-013 | UNARMOURED | 3.25" ET | 72 | 78
94 | BRACO | SSWT-014 | UNARMOURED | 3.5" ET | 78 | 83
95 | BRACO | SSWT-015 | UNARMOURED | 4" ET | 83 | 93
96 | BRACO | SSWT-016 | UNARMOURED | 4.5" ET | 93 | 104

## COVER
THERMAX LIMITED
ENVIRO
PUNE — 411 026
| TITLE |  | ELECTRICAL CABLE SCHEDULE
CLIENT
CONSULTANT
PROJECT
THERMAX O.C. NO.
THERMAX DOC. NO. / CLIENT DOC. NO.
| R0 |  | ISSUED FOR APPROVAL
| REV NO. | DATE | DESCRIPTION | PREPD. BY | CHKD. BY | APPD. BY | 5.5

## CABLE SUMMARY
REF. DRG'S.
1) EQUIPMENT LAYOUT - DRG. NO. xxxx | CABLE SPECIFICATIONS
2) ELECTRICAL LOAD LIST -DOC NO.xxxxx
LT POWER CABLES:-
NOTES:- | Sr.NO | CABLE SIZE | QTY | UNIT
| 1 | 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | 265 | Mtrs.
1) CABLE LENGTH MENTIONED ARE TENTATIVE ONLY. | 2 | 3C X 6 SQ.MM. AL. XLPE ARMOURED CABLE | 0 | Mtrs.
EXACT LENGTHS SHOULD BE MEASURED AT SITE BEFORE CUTTING | 3 | 3C X 10 SQ.MM. AL. XLPE ARMOURED CABLE | 0 | Mtrs.
THE CABLE FROM CABLE DRUM & THE CABLE LENGTHS SHOULD | 4 | 3C X 16 SQ.MM. AL. XLPE ARMOURED CABLE | 0 | Mtrs.
BE CUT ACCORDINGLY. | 5 | 3C X 35 SQ.MM. AL. XLPE ARMOURED CABLE | 0 | Mtrs.
2) CABLE ROUTE NOS. SHALL BE INCORPORATE AFTER APPROVAL | 6 | 3C X 70 SQ.MM. AL. XLPE ARMOURED CABLE | 0 | Mtrs.
OF CABLE LAYOUT. | 7 | 3C X 95 SQ.MM. AL. XLPE ARMOURED CABLE | 265 | Mtrs.
3) CABLE LENGTH MENTIONED ARE APPROXIMATE ONLY. | 8 | 3C X 185 SQ.MM. AL. XLPE ARMOURED CABLE | 0 | Mtrs.
EXACT LENGTHS SHOULD BE MEASURED AT SITE BEFORE CUTTING | 9 | 3.5C X 35 SQ.MM. AL. XLPE ARMOURED CABLE | 0 | Mtrs.
THE CABLE FROM CABLE DRUM & THE CABLE LENGTHS SHOULD | 10 | 3.5C X 70 SQ.MM. AL. XLPE ARMOURED CABLE | 0 | Mtrs.
BE CUT ACCORDINGLY. | 11 | 3.5C X 95 SQ.MM. AL. XLPE ARMOURED CABLE | 0 | Mtrs.
| 12 | 3.5C X 120 SQ.MM. AL. XLPE ARMOURED CABLE | 0 | Mtrs.
| 13 | 4C X 6 SQ.MM. AL. XLPE ARMOURED CABLE | 0 | Mtrs.
| 14 | 4C X 10 SQ.MM. AL. XLPE ARMOURED CABLE | 0 | Mtrs.
| 15 | 4C X 25 SQ.MM. AL. XLPE ARMOURED CABLE | 0 | Mtrs.
| 16 |  |  | Mtrs.
CONTROL CABLE :-
| Sr.NO | CABLE SIZE | QTY | UNIT
| 1 | 7C X 1.5 SQ.MM. CU. XLPE ARMOURED CABLE | 265 | Mtrs.
| 2 |  |  | Mtrs.
| 3 |  |  | Mtrs.
| 4 |  |  | Mtrs.

## GLAND SELECTION SHEET (hidden)
CABLE GLAND SELECTION | [8 empty] | MAKE : | COMET |  | ET
Sr.No | DESCRIPTION | CABLE OD ACTUAL | TOLERANCE (+/-) | CABLE OD WITH TOLERANCE | ENTRY AVAILABLE | GLAND SIZE SELECTED | TOTAL QTY | MAKE | GLAND CAT NO | SHROUDS DETAILS |  | 0.625 "
ARMOURED CABLES : | [11 empty] | 0.75 "
ET THREADS : | [11 empty] | 1 "
|  | 22 | 3 | 25 | PLATE | M32 | 1 | COMET | ,(IF(AND($I10=BACKUP!$B$98,($E10>=BACKUP!$F$98),($E10<=BACKUP!$G$98),($G10=BACKUP!$E$98)),(BACKUP!$C$98),(IF(AND($I10=BACKUP!$B$99,($E10>=BACKUP!$F$99),($E10<=BACKUP!$G$99),($G10=BACKUP!$E$99)),(BACKUP!$C$99),(IF(AND($I10=BACKUP!$B$100,($E10>=BACKUP!$F$100),($E10<=BACKUP!$G$100),($G10=BACKUP!$E$100)),(BACKUP!$C$100),(IF(AND($I10=BACKUP!$B$101,($E10>=BACKUP!$F$101),($E10<=BACKUP!$G$101),($G10=BACKUP!$E$101)),(BACKUP!$C$101),(IF(AND($I10=BACKUP!$B$102,($E10>=BACKUP!$F$102),($E10<=BACKUP!$G$102),($G10=BACKUP!$E$102)),(BACKUP!$C$102),(IF(AND($I10=BACKUP!$B$103,($E10>=BACKUP!$F$103),($E10<=BACKUP!$G$103),($G10=BACKUP!$E$103)),(BACKUP!$C$103),(IF(AND($I10=BACKUP!$B$104,($E10>=BACKUP!$F$104),($E10<=BACKUP!$G$104),($G10=BACKUP!$E$104)),(BACKUP!$C$104),(IF(AND($I10=BACKUP!$B$105,($E10>=BACKUP!$F$105),($E10<=BACKUP!$G$105),($G10=BACKUP!$E$105)),(BACKUP!$C$105),(IF(AND($I10=BACKUP!$B$106,($E10>=BACKUP!$F$106),($E10<=BACKUP!$G$106),($G10=BACKUP!$E$106)),(BACKUP!$C$106),(IF(AND($I10=BACKUP!$B$107,($E10>=BACKUP!$F$107),($E10<=BACKUP!$G$107),($G10=BACKUP!$E$107)),(BACKUP!$C$107),(IF(AND($I10=BACKUP!$B$108,($E10>=BACKUP!$F$108),($E10<=BACKUP!$G$108),($G10=BACKUP!$E$108)),(BACKUP!$C$108),(IF(AND($I10=BACKUP!$B$109,($E10>=BACKUP!$F$109),($E10<=BACKUP!$G$109),($G10=BACKUP!$E$109)),(BACKUP!$C$109),(IF(AND($I10=BACKUP!$B$110,($E10>=BACKUP!$F$110),($E10<=BACKUP!$G$110),($G10=BACKUP!$E$110)),(BACKUP!$C$110),(IF(AND($I10=BACKUP!$B$111,($E10>=BACKUP!$F$111),($E10<=BACKUP!$G$111),($G10=BACKUP!$E$111)),(BACKUP!$C$111),(IF(AND($I10=BACKUP!$B$112,($E10>=BACKUP!$F$112),($E10<=BACKUP!$G$112),($G10=BACKUP!$E$112)),(BACKUP!$C$112),(IF(AND($I10=BACKUP!$B$113,($E10>=BACKUP!$F$113),($E10<=BACKUP!$G$113),($G10=BACKUP!$E$113)),(BACKUP!$C$113),(IF(AND($I10=BACKUP!$B$114,($E10>=BACKUP!$F$114),($E10<=BACKUP!$G$114),($G10=BACKUP!$E$114)),(BACKUP!$C$114),(IF(AND($I10=BACKUP!$B$115,($E10>=BACKUP!$F$115),($E10<=BACKUP!$G$115),($G10=BACKUP!$E$115)),(BACKUP!$C$115),(IF(AND($I10=BACKUP!$B$116,($E10>=BACKUP!$F$116),($E10<=BACKUP!$G$116),($G10=BACKUP!$E$116)),(BACKUP!$C$116),(IF(AND($I10=BACKUP!$B$117,($E10>=BACKUP!$F$117),($E10<=BACKUP!$G$117),($G10=BACKUP!$E$117)),(BACKUP!$C$117),(IF(AND($I10=BACKUP!$B$118,($E10>=BACKUP!$F$118),($E10<=BACKUP!$G$118),($G10=BACKUP!$E$118)),(BACKUP!$C$118),(IF(AND($I10=BACKUP!$B$119,($E10>=BACKUP!$F$119),($E10<=BACKUP!$G$119),($G10=BACKUP!$E$119)),(BACKUP!$C$119),(IF(AND($I10=BACKUP!$B$120,($E10>=BACKUP!$F$120),($E10<=BACKUP!$G$120),($G10=BACKUP!$E$120)),(BACKUP!$C$120),(IF(AND($I10=BACKUP!$B$121,($E10>=BACKUP!$F$121),($E10<=BACKUP!$G$121),($G10=BACKUP!$E$121)),(BACKUP!$C$121),(IF(AND($I10=BACKUP!$B$122,($E10>=BACKUP!$F$122),($E10<=BACKUP!$G$122),($G10=BACKUP!$E$122)),(BACKUP!$C$122),(IF(AND($I10=BACKUP!$B$123,($E10>=BACKUP!$F$123),($E10<=BACKUP!$G$123),($G10=BACKUP!$E$123)),(BACKUP!$C$123),(IF(AND($I10=BACKUP!$B$124,($E10>=BACKUP!$F$124),($E10<=BACKUP!$G$124),($G10=BACKUP!$E$124)),(BACKUP!$C$124),(IF(AND($I10=BACKUP!$B$125,($E10>=BACKUP!$F$125),($E10<=BACKUP!$G$125),($G10=BACKUP!$E$125)),(BACKUP!$C$125),(IF(AND($I10=BACKUP!$B$126,($E10>=BACKUP!$F$126),($E10<=BACKUP!$G$126),($G10=BACKUP!$E$126)),(BACKUP!$C$126),(IF(AND($I10=BACKUP!$B$127,($E10>=BACKUP!$F$127),($E10<=BACKUP!$G$127),($G10=BACKUP!$E$127)),(BACKUP!$C$127),(IF(AND($I10=BACKUP!$B$128,($E10>=BACKUP!$F$128),($E10<=BACKUP!$G$128),($G10=BACKUP!$E$128)),(BACKUP!$C$128),(IF(AND($I10=BACKUP!$B$129,($E10>=BACKUP!$F$129),($E10<=BACKUP!$G$129),($G10=BACKUP!$E$129)),(BACKUP!$C$129),(IF(AND($I10=BACKUP!$B$130,($E10>=BACKUP!$F$130),($E10<=BACKUP!$G$130),($G10=BACKUP!$E$130)),(BACKUP!$C$130),(IF(AND($I10=BACKUP!$B$131,($E10>=BACKUP!$F$131),($E10<=BACKUP!$G$131),($G10=BACKUP!$E$131)),(BACKUP!$C$131),(IF(AND($I10=BACKUP!$B$132,($E10>=BACKUP!$F$132),($E10<=BACKUP!$G$132),($G10=BACKUP!$E$132)),(BACKUP!$C$132),(IF(AND($I10=BACKUP!$B$133,($E10>=BACKUP!$F$133),($E10<=BACKUP!$G$133),($G10=BACKUP!$E$133)),(BACKUP!$C$133),(IF(AND($I10=BACKUP!$B$134,($E10>=BACKUP!$F$134),($E10<=BACKUP!$G$134),($G10=BACKUP!$E$134)),(BACKUP!$C$134),(IF(AND($I10=BACKUP!$B$135,($E10>=BACKUP!$F$135),($E10<=BACKUP!$G$135),($G10=BACKUP!$E$135)),(BACKUP!$C$135),(IF(AND($I10=BACKUP!$B$136,($E10>=BACKUP!$F$136),($E10<=BACKUP!$G$136),($G10=BACKUP!$E$136)),(BACKUP!$C$136),(IF(AND($I10=BACKUP!$B$137,($E10>=BACKUP!$F$137),($E10<=BACKUP!$G$137),($G10=BACKUP!$E$137)),(BACKUP!$C$137),(IF(AND($I10=BACKUP!$B$138,($E10>=BACKUP!$F$138),($E10<=BACKUP!$G$138),($G10=BACKUP!$E$138)),(BACKUP!$C$138),(IF(AND($I10=BACKUP!$B$139,($E10>=BACKUP!$F$139),($E10<=BACKUP!$G$139),($G10=BACKUP!$E$139)),(BACKUP!$C$139),(IF(AND($I10=BACKUP!$B$140,($E10>=BACKUP!$F$140),($E10<=BACKUP!$G$140),($G10=BACKUP!$E$140)),(BACKUP!$C$140),(IF(AND($I10=BACKUP!$B$141,($E10>=BACKUP!$F$141),($E10<=BACKUP!$G$141),($G10=BACKUP!$E$141)),(BACKUP!$C$141),(IF(AND($I10=BACKUP!$B$142,($E10>=BACKUP!$F$142),($E10<=BACKUP!$G$142),($G10=BACKUP!$E$142)),(BACKUP!$C$142),(IF(AND($I10=BACKUP!$B$143,($E10>=BACKUP!$F$143),($E10<=BACKUP!$G$143),($G10=BACKUP!$E$143)),(BACKUP!$C$143),(IF(AND($I10=BACKUP!$B$144,($E10>=BACKUP!$F$144),($E10<=BACKUP!$G$144),($G10=BACKUP!$E$144)),(BACKUP!$C$144),(IF(AND($I10=BACKUP!$B$145,($E10>=BACKUP!$F$145),($E10<=BACKUP!$G$145),($G10=BACKUP!$E$145)),(BACKUP!$C$145),(IF(AND($I10=BACKUP!$B$145,($E10>=BACKUP!$F$145),($E10<=BACKUP!$G$145),($G10=BACKUP!$E$145)),(BACKUP!$C$145),(IF(AND($I10=BACKUP!$B$146,($E10>=BACKUP!$F$146),($E10<=BACKUP!$G$146),($G10=BACKUP!$E$146)),(BACKUP!$C$146),(IF(AND($I10=BACKUP!$B$147,($E10>=BACKUP!$F$147),($E10<=BACKUP!$G$147),($G10=BACKUP!$E$147)),(BACKUP!$C$147),(IF(AND($I10=BACKUP!$B$148,($E10>=BACKUP!$F$148),($E10<=BACKUP!$G$148),($G10=BACKUP!$E$148)),(BACKUP!$C$148),(IF(AND($I10=BACKUP!$B$149,($E10>=BACKUP!$F$149),($E10<=BACKUP!$G$149),($G10=BACKUP!$E$149)),(BACKUP!$C$149),(IF(AND($I10=BACKUP!$B$150,($E10>=BACKUP!$F$150),($E10<=BACKUP!$G$150),($G10=BACKUP!$E$150)),(BACKUP!$C$150),(IF(AND($I10=BACKUP!$B$151,($E10>=BACKUP!$F$151),($E10<=BACKUP!$G$151),($G10=BACKUP!$E$151)),(BACKUP!$C$151),(IF(AND($I10=BACKUP!$B$152,($E10>=BACKUP!$F$152),($E10<=BACKUP!$G$152),($G10=BACKUP!$E$152)),(BACKUP!$C$152),(IF(AND($I10=BACKUP!$B$153,($E10>=BACKUP!$F$153),($E10<=BACKUP!$G$153),($G10=BACKUP!$E$153)),(BACKUP!$C$153),(J14))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))) |  | (IF(AND($I10=BACKUP!$B$98,($E10>=BACKUP!$F$98),($E10<=BACKUP!$G$98),($G10=BACKUP!$E$98)),(BACKUP!$C$98),(IF(AND($I10=BACKUP!$B$99,($E10>=BACKUP!$F$99),($E10<=BACKUP!$G$99),($G10=BACKUP!$E$99)),(BACKUP!$C$99),(IF(AND($I10=BACKUP!$B$100,($E10>=BACKUP!$F$100),($E10<=BACKUP!$G$100),($G10=BACKUP!$E$100)),(BACKUP!$C$100),(IF(AND($I10=BACKUP!$B$101,($E10>=BACKUP!$F$101),($E10<=BACKUP!$G$101),($G10=BACKUP!$E$101)),(BACKUP!$C$101),(IF(AND($I10=BACKUP!$B$102,($E10>=BACKUP!$F$102),($E10<=BACKUP!$G$102),($G10=BACKUP!$E$102)),(BACKUP!$C$102),(IF(AND($I10=BACKUP!$B$103,($E10>=BACKUP!$F$103),($E10<=BACKUP!$G$103),($G10=BACKUP!$E$103)),(BACKUP!$C$103),(IF(AND($I10=BACKUP!$B$104,($E10>=BACKUP!$F$104),($E10<=BACKUP!$G$104),($G10=BACKUP!$E$104)),(BACKUP!$C$104),(IF(AND($I10=BACKUP!$B$105,($E10>=BACKUP!$F$105),($E10<=BACKUP!$G$105),($G10=BACKUP!$E$105)),(BACKUP!$C$105),(IF(AND($I10=BACKUP!$B$106,($E10>=BACKUP!$F$106),($E10<=BACKUP!$G$106),($G10=BACKUP!$E$106)),(BACKUP!$C$106),(IF(AND($I10=BACKUP!$B$107,($E10>=BACKUP!$F$107),($E10<=BACKUP!$G$107),($G10=BACKUP!$E$107)),(BACKUP!$C$107),(IF(AND($I10=BACKUP!$B$108,($E10>=BACKUP!$F$108),($E10<=BACKUP!$G$108),($G10=BACKUP!$E$108)),(BACKUP!$C$108),(IF(AND($I10=BACKUP!$B$109,($E10>=BACKUP!$F$109),($E10<=BACKUP!$G$109),($G10=BACKUP!$E$109)),(BACKUP!$C$109),(IF(AND($I10=BACKUP!$B$110,($E10>=BACKUP!$F$110),($E10<=BACKUP!$G$110),($G10=BACKUP!$E$110)),(BACKUP!$C$110),(IF(AND($I10=BACKUP!$B$111,($E10>=BACKUP!$F$111),($E10<=BACKUP!$G$111),($G10=BACKUP!$E$111)),(BACKUP!$C$111),(IF(AND($I10=BACKUP!$B$112,($E10>=BACKUP!$F$112),($E10<=BACKUP!$G$112),($G10=BACKUP!$E$112)),(BACKUP!$C$112),(IF(AND($I10=BACKUP!$B$113,($E10>=BACKUP!$F$113),($E10<=BACKUP!$G$113),($G10=BACKUP!$E$113)),(BACKUP!$C$113),(IF(AND($I10=BACKUP!$B$114,($E10>=BACKUP!$F$114),($E10<=BACKUP!$G$114),($G10=BACKUP!$E$114)),(BACKUP!$C$114),(IF(AND($I10=BACKUP!$B$115,($E10>=BACKUP!$F$115),($E10<=BACKUP!$G$115),($G10=BACKUP!$E$115)),(BACKUP!$C$115),(IF(AND($I10=BACKUP!$B$116,($E10>=BACKUP!$F$116),($E10<=BACKUP!$G$116),($G10=BACKUP!$E$116)),(BACKUP!$C$116),(IF(AND($I10=BACKUP!$B$117,($E10>=BACKUP!$F$117),($E10<=BACKUP!$G$117),($G10=BACKUP!$E$117)),(BACKUP!$C$117),(IF(AND($I10=BACKUP!$B$118,($E10>=BACKUP!$F$118),($E10<=BACKUP!$G$118),($G10=BACKUP!$E$118)),(BACKUP!$C$118),(IF(AND($I10=BACKUP!$B$119,($E10>=BACKUP!$F$119),($E10<=BACKUP!$G$119),($G10=BACKUP!$E$119)),(BACKUP!$C$119),(IF(AND($I10=BACKUP!$B$120,($E10>=BACKUP!$F$120),($E10<=BACKUP!$G$120),($G10=BACKUP!$E$120)),(BACKUP!$C$120),(IF(AND($I10=BACKUP!$B$121,($E10>=BACKUP!$F$121),($E10<=BACKUP!$G$121),($G10=BACKUP!$E$121)),(BACKUP!$C$121),(IF(AND($I10=BACKUP!$B$122,($E10>=BACKUP!$F$122),($E10<=BACKUP!$G$122),($G10=BACKUP!$E$122)),(BACKUP!$C$122),(IF(AND($I10=BACKUP!$B$123,($E10>=BACKUP!$F$123),($E10<=BACKUP!$G$123),($G10=BACKUP!$E$123)),(BACKUP!$C$123),(IF(AND($I10=BACKUP!$B$124,($E10>=BACKUP!$F$124),($E10<=BACKUP!$G$124),($G10=BACKUP!$E$124)),(BACKUP!$C$124),(IF(AND($I10=BACKUP!$B$125,($E10>=BACKUP!$F$125),($E10<=BACKUP!$G$125),($G10=BACKUP!$E$125)),(BACKUP!$C$125),(IF(AND($I10=BACKUP!$B$126,($E10>=BACKUP!$F$126),($E10<=BACKUP!$G$126),($G10=BACKUP!$E$126)),(BACKUP!$C$126),(IF(AND($I10=BACKUP!$B$127,($E10>=BACKUP!$F$127),($E10<=BACKUP!$G$127),($G10=BACKUP!$E$127)),(BACKUP!$C$127),(IF(AND($I10=BACKUP!$B$128,($E10>=BACKUP!$F$128),($E10<=BACKUP!$G$128),($G10=BACKUP!$E$128)),(BACKUP!$C$128),(IF(AND($I10=BACKUP!$B$129,($E10>=BACKUP!$F$129),($E10<=BACKUP!$G$129),($G10=BACKUP!$E$129)),(BACKUP!$C$129),(IF(AND($I10=BACKUP!$B$130,($E10>=BACKUP!$F$130),($E10<=BACKUP!$G$130),($G10=BACKUP!$E$130)),(BACKUP!$C$130),(IF(AND($I10=BACKUP!$B$131,($E10>=BACKUP!$F$131),($E10<=BACKUP!$G$131),($G10=BACKUP!$E$131)),(BACKUP!$C$131),(IF(AND($I10=BACKUP!$B$132,($E10>=BACKUP!$F$132),($E10<=BACKUP!$G$132),($G10=BACKUP!$E$132)),(BACKUP!$C$132),(IF(AND($I10=BACKUP!$B$133,($E10>=BACKUP!$F$133),($E10<=BACKUP!$G$133),($G10=BACKUP!$E$133)),(BACKUP!$C$133),(IF(AND($I10=BACKUP!$B$134,($E10>=BACKUP!$F$134),($E10<=BACKUP!$G$134),($G10=BACKUP!$E$134)),(BACKUP!$C$134),(IF(AND($I10=BACKUP!$B$135,($E10>=BACKUP!$F$135),($E10<=BACKUP!$G$135),($G10=BACKUP!$E$135)),(BACKUP!$C$135),(IF(AND($I10=BACKUP!$B$136,($E10>=BACKUP!$F$136),($E10<=BACKUP!$G$136),($G10=BACKUP!$E$136)),(BACKUP!$C$136),(IF(AND($I10=BACKUP!$B$137,($E10>=BACKUP!$F$137),($E10<=BACKUP!$G$137),($G10=BACKUP!$E$137)),(BACKUP!$C$137),(IF(AND($I10=BACKUP!$B$138,($E10>=BACKUP!$F$138),($E10<=BACKUP!$G$138),($G10=BACKUP!$E$138)),(BACKUP!$C$138),(IF(AND($I10=BACKUP!$B$139,($E10>=BACKUP!$F$139),($E10<=BACKUP!$G$139),($G10=BACKUP!$E$139)),(BACKUP!$C$139),(IF(AND($I10=BACKUP!$B$140,($E10>=BACKUP!$F$140),($E10<=BACKUP!$G$140),($G10=BACKUP!$E$140)),(BACKUP!$C$140),(IF(AND($I10=BACKUP!$B$141,($E10>=BACKUP!$F$141),($E10<=BACKUP!$G$141),($G10=BACKUP!$E$141)),(BACKUP!$C$141),(IF(AND($I10=BACKUP!$B$142,($E10>=BACKUP!$F$142),($E10<=BACKUP!$G$142),($G10=BACKUP!$E$142)),(BACKUP!$C$142),(IF(AND($I10=BACKUP!$B$143,($E10>=BACKUP!$F$143),($E10<=BACKUP!$G$143),($G10=BACKUP!$E$143)),(BACKUP!$C$143),(IF(AND($I10=BACKUP!$B$144,($E10>=BACKUP!$F$144),($E10<=BACKUP!$G$144),($G10=BACKUP!$E$144)),(BACKUP!$C$144),(IF(AND($I10=BACKUP!$B$145,($E10>=BACKUP!$F$145),($E10<=BACKUP!$G$145),($G10=BACKUP!$E$145)),(BACKUP!$C$145),(IF(AND($I10=BACKUP!$B$145,($E10>=BACKUP!$F$145),($E10<=BACKUP!$G$145),($G10=BACKUP!$E$145)),(BACKUP!$C$145),(IF(AND($I10=BACKUP!$B$146,($E10>=BACKUP!$F$146),($E10<=BACKUP!$G$146),($G10=BACKUP!$E$146)),(BACKUP!$C$146),(IF(AND($I10=BACKUP!$B$147,($E10>=BACKUP!$F$147),($E10<=BACKUP!$G$147),($G10=BACKUP!$E$147)),(BACKUP!$C$147),(IF(AND($I10=BACKUP!$B$148,($E10>=BACKUP!$F$148),($E10<=BACKUP!$G$148),($G10=BACKUP!$E$148)),(BACKUP!$C$148),(IF(AND($I10=BACKUP!$B$149,($E10>=BACKUP!$F$149),($E10<=BACKUP!$G$149),($G10=BACKUP!$E$149)),(BACKUP!$C$149),(IF(AND($I10=BACKUP!$B$150,($E10>=BACKUP!$F$150),($E10<=BACKUP!$G$150),($G10=BACKUP!$E$150)),(BACKUP!$C$150),(IF(AND($I10=BACKUP!$B$151,($E10>=BACKUP!$F$151),($E10<=BACKUP!$G$151),($G10=BACKUP!$E$151)),(BACKUP!$C$151),(IF(AND($I10=BACKUP!$B$152,($E10>=BACKUP!$F$152),($E10<=BACKUP!$G$152),($G10=BACKUP!$E$152)),(BACKUP!$C$152),(IF(AND($I10=BACKUP!$B$153,($E10>=BACKUP!$F$153),($E10<=BACKUP!$G$153),($G10=BACKUP!$E$153)),(BACKUP!$C$153),(J14))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))))) | 1.25 "
[9 empty] | NA |  |  | 1.5 "
NA
METRIC THREADS : | [11 empty] | 2 "
|  | 16 | 2 | 18 | PLATE | M32 | 0 | COMET | NA |  |  | 2.5 "
3 "
3.25 "
NPT THREADS : | [11 empty] | 3.5 "
|  | 31 | 2 | 33 | PLATE | 1/2 " NPT | 0 | COMET | NA |  |  | 4 "
4.5 "
MET
UNARMOURED CABLES : | [11 empty] | M16
|  | 40 | 2 | 42 | PLATE |  | 0 | COMET | NA |  |  | M20
M25
M32
M40
M50
M63
M75
M82
M90
M100
M115
NPT
1/2 " NPT
3/4 " NPT
1 " NPT
1.25 " NPT
1.5 " NPT
2 " NPT
2.5 " NPT
3 " NPT
3.5 " NPT
UNAR
0.75 "
1 "
1.25 "
1.5 "
40 MM
42 MM
2 "
2.5 "
70 MM
3 "
3.25 "
3.5 "
3.75 "
4 "
4.5 "
M28
M40
M42
M70

## GLAND SUMMARY
REF.
1) BRACO MAKE, Ni PLATED BRASS, DC CABLE GLANDS CATALOGUE | CABLE SPECIFICATIONS |  |  |  | -176
CABLE GLAND SUMMARY :
NOTES:- | Sr.NO | GLAND CAT NO. | QTY | UNIT
1) PVC SHROUDS SHALL BE PROVIDED FOR CABLE GLANDS WHICH ARE | 1 | BPW 01 | 224 | Nos
LOCATED OUTSIDE MCC ROOM. | 2 | BPW 02 | 5 | Nos
| 3 | BPW 03 | 32 | Nos
| 4 | BPW 04 | 8 | Nos
| 5 | BPW 05 | 14 | Nos
| 6 | BPW 06 | 16 | Nos
| 7 | BPW 07 | 10 | Nos
| 8 | BPW 08 | 7 | Nos
| 9 | BPW 01 WITH M20 THREAD | 52 | Nos
| 10 | BPW 02S WITH M20 THREAD | 3 | Nos
| 11 | BPW 03 WITH M25 THREAD | 16 | Nos
| 12 | BPW 04 WITH M25 THREAD | 2 | Nos
| 13 | BPW 06 WITH M40 THREAD | 16 | Nos
| 14 | BPW 07 WITH M40 THREAD | 2 | Nos
| 15 | BPW 07 WITH M50 THREAD | 2 | Nos
| 16 | BPW 08 WITH M50 THREAD | 7 | Nos
PVC SHROUD SUMMARY :
| Sr.NO | CABLE SIZE | QTY | UNIT
| 1 | PVC SHROUD FOR BPW 01 | 131 | Nos
| 2 | PVC SHROUD FOR BPW 02 | 1 | Nos
| 3 | PVC SHROUD FOR BPW 02S | 3 | Nos
| 4 | PVC SHROUD FOR BPW 03 | 22 | Nos
| 5 | PVC SHROUD FOR BPW 04 | 5 | Nos
| 6 | PVC SHROUD FOR BPW 05 | 7 | Nos
| 7 | PVC SHROUD FOR BPW 06 | 16 | Nos
| 8 | PVC SHROUD FOR BPW 07 | 7 | Nos
| 9 | PVC SHROUD FOR BPW 08 | 7 | Nos
| 10 |  |  | Nos

## MCC CABLE SCHDULE
CABLE SCHEDULE
Project:
| CLIENT :- | [36 empty] | PLEASE DO NOT DELETE THESE COLOUMNS
| THERMAX OC. NO :- | [37 empty] | NICKEL PLATED BRASS | [10 empty] | SS304
[32 empty] | LADDER POWER |  | LADDER CONTROL | [5 empty] | FOR FROM SIDE |  |  |  |  | FOR TO SIDE |  |  |  |  | FOR FROM SIDE |  |  |  |  | FOR TO SIDE
CABLE SCHEDULE
SR. NO. | CABLE NO. | CABLE TAG | FEEDER NO | FROM TB NO | FROM FERRULE NO | FROM PANEL / JB NO | FROM PANEL / JB DESCRIPTION | SYSTEM VOLTAGE | KW RATING | Type | CABLE SIZE | CABLE TYPE | TO FERRULE NO | TO EQUIPMENT NO | TAG NOS. | TO TB NO. | TO EQUIPMENT DESCRIPTION | CABLE LENGTH (IN MTR.) | CABLE OD | ENTRY AVAILABLE AT PANEL / JB | SIZE SELECTED AT PANEL / JB | GLAND CAT NO AT PANEL / JB | SHROUD REQUIREMENT AT PANEL / JB | SHROUD CAT NO AT PANEL / JB | ENTRY AVAILABLE AT EQUIPMENT | SIZE SELECTED AT EQUIPMENT | GLAND CAT NO AT EQUIPMENT | SHROUD REQUIREMENT AT EQUIPMENT | SHROUD CAT NO AT EQUIPMENT | CABLE TRAY ROUTING | REMARK | 50W | 100W | 50W | 100W | SCOPE |  | TYPE OF CABLE | MAKE |  | ET | METRIC | NPT | UNARMOURED |  | ET | METRIC | NPT | UNARMOURED |  | ET | METRIC | NPT | UNARMOURED |  | ET | METRIC | NPT | UNARMOURED
MCC PANEL
1 | PC-01 | PC-01/MCC-1-PM-WTP-M-02-A | 2f1 | PT-10 | PM-WTP-M-02-A - U1/PT-10 | MCC-1 | MCC PANEL | 415 VAC | 37 | DOL | 3C X 95 SQ.MM. AL. XLPE ARMOURED CABLE | A2XFY | PT-10/PM-WTP-M-02-A - U1 | PM-WTP-M-02-A - U1 | PM-WTP-M-02-A | U1 | MMF BACKWASH PUMP-A | 265 | 34 | Plate | 1.5" ET | BPW 07 | YES | PVC SHROUD FOR BPW 07 | M40 | 1.5" ET | BPW 07 | YES | PVC SHROUD FOR BPW 07 | CT001,CT005,CT006,CT009,CT011,CT015,CT025,CT029,CT031,CT033,CT034 |  |  | 3 |  |  |  | L1 | ARMOURED CABLE | BRACO | ET | BPW 07 | NA | NA | NA | ET | BPW 07 | NA | NA | NA | ET | SSW 07 | NA | NA | NA | ET | SSW 07 | NA | NA | NA
|  |  | 2f1 | PT-2 | PM-WTP-M-02-A - V1/PT-2 | [7 empty] | PT-2/PM-WTP-M-02-A - V1 | PM-WTP-M-02-A - V1 |  | V1 | [16 empty] | 3 |  |  |  | L1 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
|  |  | 2f1 | PT-3 | PM-WTP-M-02-A - W1/PT-3 | [7 empty] | PT-3/PM-WTP-M-02-A - W1 | PM-WTP-M-02-A - W1 |  | W1 | [16 empty] | 3 |  |  |  | L1 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
| PC-02 | PC-02/MCC-1-PM-WTP-M-02-A-SH | 1F1 | PT-4 | PM-WTP-M-02-A-SH - SH.TB-1/PT-4 |  |  |  |  | -- | 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | 2XWY | PT-4/PM-WTP-M-02-A-SH - SH.TB-1 | PM-WTP-M-02-A-SH - SH.TB-1 | PM-WTP-M-02-A-SH | SH.TB-1 | SPACE HEATER FOR MMF BACKWASH PUMP-A | 265 | 17 | Plate | 0.75" ET | BPW 01 | NO | NA | M20 | 0.75" ET | BPW 01 | YES | PVC SHROUD FOR BPW 01 | CT001,CT005,CT006,CT009,CT011,CT015,CT025,CT029,CT031,CT033,CT034 | [6 empty] | L3 | ARMOURED CABLE | BRACO | ET | BPW 01 | NA | NA | NA | ET | BPW 01 | NA | NA | NA | ET | SSW 01 | NA | NA | NA | ET | SSW 01 | NA | NA | NA
|  |  | 1F1 | PT-5 | PM-WTP-M-02-A-SH - SH.TB-2/PT-5 |  |  |  |  | -- |  |  | PT-5/PM-WTP-M-02-A-SH - SH.TB-2 | PM-WTP-M-02-A-SH - SH.TB-2 |  | SH.TB-2 | [20 empty] | L3 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
| CC-01 | CC-01/MCC-1-PM-WTP-M-02-A-LPBS | 1F1 | 1X1 | PM-WTP-M-02-A-LPBS - TB-1/1X1 |  |  |  |  | -- | 7C X 1.5 SQ.MM. CU. XLPE ARMOURED CABLE | 2XWY | 1X1/PM-WTP-M-02-A-LPBS - TB-1 | PM-WTP-M-02-A-LPBS - TB-1 | PM-WTP-M-02-A-LPBS | TB-1 | LPBS FOR MMF BACKWASH PUMP-A | 265 | 18 | Plate | 0.75" ET | BPW 01 | NO | NA | -- | 0.75" ET | BPW 01 | YES | PVC SHROUD FOR BPW 01 | CTC001,CTC005,CTC006,CTC009,CTC011,CTC015,CTC025,CTC029,CTC031,CTC033,CTC034 |  |  |  | 3 |  |  | C1 | ARMOURED CABLE | BRACO | ET | BPW 01 | NA | NA | NA | ET | BPW 01 | NA | NA | NA | ET | SSW 01 | NA | NA | NA | ET | SSW 01 | NA | NA | NA
|  | CC-01/MCC-1- | 1F1 | 1X1 | PM-WTP-M-02-A-LPBS - TB-2/1X1 |  |  |  |  | -- |  |  | 1X1/PM-WTP-M-02-A-LPBS - TB-2 | PM-WTP-M-02-A-LPBS - TB-2 |  | TB-2 | [17 empty] | 3 |  |  | C1 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
|  | CC-01/MCC-1- | 1F1 | 1X1 | PM-WTP-M-02-A-LPBS - TB-3/1X1 |  |  |  |  | -- |  |  | 1X1/PM-WTP-M-02-A-LPBS - TB-3 | PM-WTP-M-02-A-LPBS - TB-3 |  | TB-3 | [17 empty] | 3 |  |  | C1 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
|  | CC-01/MCC-1- | 1F1 | 1X1 | PM-WTP-M-02-A-LPBS - TB-4/1X1 |  |  |  |  | -- |  |  | 1X1/PM-WTP-M-02-A-LPBS - TB-4 | PM-WTP-M-02-A-LPBS - TB-4 |  | TB-4 | [17 empty] | 3 |  |  | C1 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
|  | CC-01/MCC-1- | 1F1 | 1X1 | PM-WTP-M-02-A-LPBS - TB-5/1X1 |  |  |  |  | -- |  |  | 1X1/PM-WTP-M-02-A-LPBS - TB-5 | PM-WTP-M-02-A-LPBS - TB-5 |  | TB-5 | [17 empty] | 3 |  |  | C1 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
|  | CC-01/MCC-1- | 1F1 | 1X1 | PM-WTP-M-02-A-LPBS - TB-6/1X1 |  |  |  |  | -- |  |  | 1X1/PM-WTP-M-02-A-LPBS - TB-6 | PM-WTP-M-02-A-LPBS - TB-6 |  | TB-6 | [17 empty] | 3 |  |  | C1 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
|  | CC-01/MCC-1- | 1F1 | 1X1 | PM-WTP-M-02-A-LPBS - TB-7/1X1 |  |  |  |  | -- |  |  | 1X1/PM-WTP-M-02-A-LPBS - TB-7 | PM-WTP-M-02-A-LPBS - TB-7 |  | TB-7 | [17 empty] | 3 |  |  | C1 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
2 | IC-01 | IC-01/PLC CUM STARTER PANEL-/LIP-1 - TBA-1 |  |  | LIP-1 - TBA-1/ | PCSP | PLC CUM STARTER PANEL | 4-20mA | -- | -- | 6P X 1 SQ.MM. CU. ARMOURED CABLE | 2XWY | /LIP-1 - TBA-1 | LIP-1 - TBA-1 | LIP-1 | TBA-1 | LOCAL INDICATION PANEL RO) | 270 | 20 | Plate | 0.75" ET | BPW 02S | NO | NA | M40 | 0.75" ET | BPW 02S | YES | PVC SHROUD FOR BPW 02S | CT001,CT005,CT006,CT009,CT011,CT015,CT025,CT029,CT031,CT033,CT032 |  |  | 3 |  |  |  | L1 | ARMOURED CABLE | BRACO | ET | BPW 02S | NA | NA | NA | ET | BPW 02S | NA | NA | NA | ET | SSW 02S | NA | NA | NA | ET | SSW 02S | NA | NA | NA
[5 empty] | LIP-1 - TBA-2/ |  |  |  | -- |  |  |  | /LIP-1 - TBA-2 | LIP-1 - TBA-2 |  | TBA-2 | [20 empty] | L2 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
[5 empty] | LIP-1 - TBA-3/ |  |  |  | -- |  |  |  | /LIP-1 - TBA-3 | LIP-1 - TBA-3 |  | TBA-3 | [20 empty] | L3 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
[5 empty] | LIP-1 - TBA-4/ | [7 empty] | /LIP-1 - TBA-4 | LIP-1 - TBA-4 |  | TBA-4 | [17 empty] | 3 |  |  | C1 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
[5 empty] | / | [7 empty] | /LIP-1 - TBA-5 | LIP-1 - TBA-5 |  | TBA-5 | [16 empty] | 3 |  |  |  | L1 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
[5 empty] | / | [7 empty] | /LIP-1 - TBA-6 | LIP-1 - TBA-6 |  | TBA-6 | [20 empty] | L2 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
[5 empty] | / | [7 empty] | /LIP-1 - TBA-7 | LIP-1 - TBA-7 |  | TBA-7 | [20 empty] | L3 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
[5 empty] | / | [7 empty] | /LIP-1 - TBA-8 | LIP-1 - TBA-8 |  | TBA-8 | [17 empty] | 3 |  |  | C1 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
[5 empty] | / | [7 empty] | /LIP-1 - TBA-9 | LIP-1 - TBA-9 |  | TBA-9 | [15 empty] | 3 |  |  |  |  | L1 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
[5 empty] | / | [7 empty] | /LIP-1 - TBA-10 | LIP-1 - TBA-10 |  | TBA-10 | [17 empty] | 3 |  |  | C1 |  | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
[39 empty] | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
VFD PANEL | [38 empty] | BRACO |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA |  | NA | NA | NA | NA
Note on D7: Author: KEEP BLANK WILL BE FILLED AFTER RECEIPT OF VENDOR DRAWING
Note on E7: Author: KEEP BLANK WILL BE FILLED AFTER RECEIPT OF VENDOR DRAWING
Note on G7: Author: MANUAL ENTRY
Note on H7: Author: FROM PROJECT INFORMATION UI
Note on I7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 415VAC 230 VAC 110 VAC 4-20 mA
Note on P7: Author: MOTOR TAG THIS WILL COME FROM LOAD LIIST
Note on R7: Author: THIS WILL COME FROM LOAD LIST
Note on U7: FOR PANEL SIDE, PLATE WILL BE DEFAULT ENTRY
Note on V7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MANUAL SELECTION
Note on W7: SUMMARY TO BE CRAETED BASED ON THIS COLUMN DATA
Note on X7: DEFAULT VALUE WILL BE NO
Note on Y7: Author: Do not fill / edit anything in this coloumn AUTO SELECTION
Note on Z7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MANUAL SELECTION
Note on AA7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: MANUAL SELECTION
Note on AB7: SUMMARY TO BE CRAETED BASED ON THIS COLUMN DATA
Note on AC7: THIS WILL BE POPUKATED FROM ELECTRICAL LOAD LIST
Note on AD7: Author: Do not fill / edit anything in this coloumn AUTO SELECTION
Note on AE7: Author: DEFAULT HIDE

## GLAND SELEC. INPUT & NOTES SHT
INSTRUCTIONS & NOTES FOR SELECTION OF WEATHER PROOF DOUBLE COMPRESSION CABLE GLANDS USING THIS CABLE SCHEDULE
Notes :
1 | This Excel is for selection of Weather Proof Double compression cable glands for Armoured / Unarmoured cables.
2 | This Excel has been prepared with Standard cable gland CAT No's of make Braco & Comet.
3 | This Excel can be used for selection of all type of cable entries i.e. ET, Metric, NPT.
4 | This Excel has been prepared with cable gland MOC of Nickel Plate Brass & SS304.
(SS304 MOC for Make Braco make only.)
Instructions to use :
1 | Select the cable gland Make & MOC as per the project requirement. (Discuss with respective buyer & PM for the make)
|  | 1 | SELECT GLAND MAKE : | BRACO
|  | 2 | SELECT GLAND MOC : | Ni PLATED BRASS
2 | Please do not shift any rows / coloumns in cable schedule sheet.
3 | Cable size description should be as follows do not change the format/sequence(ex. Space) of the description. It should be always
end with either "ARMOURED CABLE" or "UNARMOURED CABLE".
| Ex . | a) "3C x 2.5 SQ.MM. CU. XLPE/PVC ARMOURED CABLE"
b) "3C x 2.5 SQ.MM. CU. XLPE/PVC UNARMOURED CABLE"
c) "1PR X 1.0 SQ.MM. CU. XLPE/PVC ARMOURED CABLE"
4 | Fill the cable types & OD below. ( Take exact OD from test report(recommended). If exact OD not available mention OD with specificied
tolerance in final datasheet.)
|  | Sr.No | Cable Size (Discription shall be same as cable schedule) | Cable OD
|  | 1 | 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | 17
|  | 2 | 3C X 6 SQ.MM. AL. XLPE ARMOURED CABLE | 20
|  | 3 | 3C X 10 SQ.MM. AL. XLPE ARMOURED CABLE | 21
|  | 4 | 3C X 16 SQ.MM. AL. XLPE ARMOURED CABLE | 21
|  | 5 | 3C X 35 SQ.MM. AL. XLPE ARMOURED CABLE | 24.5
|  | 6 | 3C X 70 SQ.MM. AL. XLPE ARMOURED CABLE | 30.5
|  | 7 | 3C X 95 SQ.MM. AL. XLPE ARMOURED CABLE | 34
|  | 8 | 3.5C X 120 SQ.MM. AL. XLPE ARMOURED CABLE | 42
|  | 9 | 3.5C X 35 SQ.MM. AL. XLPE ARMOURED CABLE | 28
|  | 10 | 3.5C X 70 SQ.MM. AL. XLPE ARMOURED CABLE | 35
|  | 11 | 3.5C X 95 SQ.MM. AL. XLPE ARMOURED CABLE | 39
|  | 12 | 4C X 10 SQ.MM. AL. XLPE ARMOURED CABLE | 22
|  | 13 | 6P X 1 SQ.MM. CU. ARMOURED CABLE | 20
|  | 14 | 7C X 1.5 SQ.MM. CU. XLPE ARMOURED CABLE | 18
5 | In "cable schedule" sheet "FROM / TO SIDE ENTRY AVAILABLE" coloumn fill the availabe Entry as per the Equipment / Instrument datasheet.
6 | In "cable schedule" sheet "FROM / TO SIDE SIZE SELECTED" coloumn if the entry available is "Plate" Select the ET size (start from minimum size to
maximum size to obtain the Gland CAT No. and if not plate select the same size as Available entry.
7 | If the above Instructions followed properly Gland CAT would have been generated automatically by now. If not it might be non standard requirement
please select the cable gland as per the respective cable gland catalogues.
8 | After that In "cable schedule" Sheet "FROM / TO SIDE SHROUD REQUIREMENT" Coloumn Select either "Yes" or "No" as per the requirement.
(Note PVC Shroud shall be used for all Glands which are outside MCC / Control Room)
9 | After Selection of Shroud requirement Shroud CAT No. would have been generated automatically by now.
10 | After completion of All cable gland selection Hide the "To be hide" coloumn while submitting to client.