## COVER
THERMAX LIMITED
WATER & WASTE SOLUTION
PUNE - 411 026
TITLE
CLIENT
CONSULTANT
PROJECT
THERMAX O.C. NO.
THERMAX DOC. NO. / CLIENT DOC. NO.
| REV NO. | DATE | DESCRIPTION | PREPD. BY | CHKD. BY | APPD. BY | 5.5

## INSTRUCTION PAGE
OC NO XXX -INSTRUCTIONS TO LOCAL PUSH BUTTON STATIONS VENDORS
OFFER :
Offer for the LPBS shall be based on following documents enclosed.
Sr.No. | Item Description | Document Number | Pages
1 | MOTOR SPECIFICATION | To be Mentioned
2 | MOTOR LIST | To be Mentioned
3
4
The offer shall be strictly based on the document mentioned above. Deviations if any shall be clearly highlighted in the offer in the deviations format enclosed, otherwise it is presumed that there is no deviation. Vendor shall obtain the necessary clarity from Thermax regarding the discrepancy if any in the specifications furnished. Technical literature shall be furnished along with the offer. Vendor shall enclose along with his offer the purchase specifications of Thermax stamped as "Accepted ". Offer not in line with the above shall be summarily rejected. Offer complete in all respects should be received by us within 6 days from date of this enquiry.
B) DRAWING SUBMISSION :
Following documents shall be submitted to us for our / our client’s approval in '1' sets. However drawing submission, approval, inspection and / or certification does neither relieve the vendor of his responsibility for furnishing the equipment confirming to the requirement of purchase specification nor prejudice any claim.
ALONG WITH THE OFFER |  | AFTER PLACEMENT OF ORDER | TIME
Along with the offer 1. Signed & stamped inquiry document 2. Motor data sheet, Motor GA, TB GA etc. 3. Deviation list ( if any ) 4. List of spares provided as per specs (if any) 5. QAP 6. Technical Literature |  | After placement of order 1. Motor data sheet , Motor & terminal box GA drawings 2. Characteristic Curves a) torque vs speed b) current vs speed c) current vs time d) thermal withstand ( hot & cold ) 3. Any other doc./drg. as mentioned in specs enclosed/required by our clients. | 3 Days
B) | Vendor shall refer motor list for final cable size. Vendor shall provide terminal
box, TB & cable entry suitable for final cable sizes indicated by us. The drawings submitted shall be
legible and correct as per specification & shall not call for resubmission.
C) | FINAL DOCUMENTATION :
Vendor shall submit '01' sets of O&M manuals to our office.
D) | IMPORTANT NOTES:
1) | Motors shall be suitable for "torque v/s speed" characteristics of driven equipt which shall be furnished
later.
2) | If load GD2 value is not furnished, load GD2 may be considered equal to motor GD2.
3) | To select motor rating, consider pumps discharge valve in open condition.
4) | To select motor rating, consider blowers damper in open condition
5) | Motor Data-sheets, curves & Drawings shall be submitted in a single PDF file.
6) | Vendor shall select the appropriate motor (frame size, bearings etc.) based on type of motor starter
(DOL/VFD/Star-delta/Soft starter), type of coupling & driven equipment/application.
7) | Vendor to submit this document duly signed & stamped for our records.
8) | Any deviation on this Motor Specifications Vendor has to convey the same at Bid Stage only.
During detail Engineering any deviation shall not be entertained.
9) | Main Terminal Box Add On Cost for Higher size TB shall be given with the Offer. Maximum Cable Size
for the Terminal Box shall be confirmed during Bid stage only.

## SPECIFICATION
MOTOR GENERAL SPECIFICATIONS:
Sr. No. | SPECIFICATIONS | SAFE AREA | HAZARDOUS AREA
A | DESIGN PARAMETER
1 | Area Classification | None, None, None, None | None, None, None, None
2 | Ambient Temperature [Max] | 40 | 40
3 | Ambient Temperature [Min] | 40 | 40
4 | Electrical Design Temperature | 50 | 50
5 | Humidity [Max] | 85 | 85
6 | Humidity [Min] | 35 | 35
7 | Humidity Average | 65 | 65
8 | Humidity Performance. | 65 | 65
9 | Altitude (Site Nominal Elevation) | 750 | 750
10 | Seismic Zone | 2 | 2
B | ELECTRICAL PARAMETER
1 | Supply Voltage | 415 VAC | 415 VAC
2 | Phase | 3 Phase / 4 Wire | 3 Phase / 4 Wire
3 | Frequency | 50 | 50
4 | Fault Level For System | 50 | 50
5 | Fault Level For Terminal Box | 50 KA for 0.25 Sec. for motors | 50 KA for 0.25 Sec. for motors
C | MECHANICAL PARAMETER
1 | Design, Construction, Performance, Efficiency & Testing Standards | IEC 61439 | IEC-60034 / IS 12615 (latest revision)
2 | Type | Low Voltage Squirrel Cage Induction Motor | Low Voltage Squirrel Cage Induction Motor
3 | Motor Winding MOC | Copper | Copper
4 | Protection Class For All Motors | IP55 | IP55
5 | Duty cycle | S1 | S1
6 | Method of starting: | DOL -- as per attached motor list | DOL -- as per attached motor list
|  | STAR/DELTA -- as per attached motor list | STAR/DELTA -- as per attached motor list
|  | VFD -- as per attached motor list | VFD -- as per attached motor list
|  | RDOL -- as per attached motor list | RDOL -- as per attached motor list
7 | Insulation Class | Class-F | Class-F
8 | Temp. rise limited to | Class-B | Class-B
9 | Lifting Eye Bolt
10 | Starts / Hour permissibe | 2 Hot and 3 Cold | 2 Hot and 3 Cold
11 | Service Factor | 1 | 1
12 | Type of Cooling | TEFC | TEFC
13 | Starting current | Shall be as per IS 12615 | Shall be as per IS 12615
14 | Vibrations Level | as per IS 12075-1986/ IEC 60034 | as per IS 12075-1986/ IEC 60034
15 | Noise Level | <85 dBA (for Continuous Operating Equipments @ 1.5 mtr) & <92dBA (for Feed water pumps @ 1mtr) | <85 dBA (for Continuous Operating Equipments @ 1.5 mtr) & <92dBA (for Feed water pumps @ 1mtr)
16 | Torque | max torque shall not be less than 200% of full load torque | max torque shall not be less than 200% of full load torque
17 | Earthing | Motor Body & TB Earthing Terminal To be provided. | Motor Body & TB Earthing Terminal To be provided.
18 | Frame Material
19 | Material of Terminal Box | IP55 | IP55
20 | Terminal Box Location
21 | Cable Entry For Terminal Box
22 | Paint Type & Shade | User Defined | User Defined
23 | Motor Ratings | As per Motor List | As per Motor List
24 | No. of Pole requirement | As per Motor List | As per Motor List
25 | Type of Starting Method | As per Motor List | As per Motor List
26 | Type of Mounting | As per Motor List | As per Motor List
27 | Efficiency Class | As per Motor List | As per Motor List
D | GENEARL PARAMETER
1 | Direction of Roration | Bidirection | Bidirection
2 | Space Heater | As per Motor List | As per Motor List
3 | Thermistor (PTC) | As per Motor List | As per Motor List
4 | Winding Temperature RTD (PT-100) Simplex / Duplex | As per Motor List | As per Motor List
5 | Bearing Temperature BTD (PT-100) Simplex / Duplex | As per Motor List | As per Motor List
6 | Bearing Vibration sensor Mounting Provision | For Drive & Non Drive end - X axis - 1No. Each. | For Drive & Non Drive end - X axis - 1No. Each.
7 | Bearing Vibration sensor Tapping Details | M8 x 1.25mm (pitch) - 15 mm long | M8 x 1.25mm (pitch) - 15 mm long
8 | Inspection | a) OEM to submit their QAP for TL QC approval. b) Refer TL QA Quality requirment Sheet - as part of RFQ. | a) OEM to submit their QAP for TL QC approval. b) Refer TL QA Quality requirment Sheet - as part of RFQ.
9 | Accessories: | For VFD motors:- 1. Windings shall be VPI treated & 2 coats enameled / suitable for VFD operations. 2. NDE side bearing shall be insulated type.(Rating Cut-off shall be as per OEM Std.) However, for Insulated bearing for DE side shall be decided by motor Vendor. 3. Motors shall be sized to operate satisfactorily under the lowest speed Conditions. | For VFD motors:- 1. Windings shall be VPI treated & 2 coats enameled / suitable for VFD operations. 2. NDE side bearing shall be insulated type.(Rating Cut-off shall be as per OEM Std.) However, for Insulated bearing for DE side shall be decided by motor Vendor. 3. Motors shall be sized to operate satisfactorily under the lowest speed Conditions.
10 | Make | As Per Approved Make List | As Per Approved Make List
11 | Notes: | 1. Two nos. Earthing pads (one on each side) to be provided on all motors. 2. All motors after achieving full operating temperature shall be capable of withstanding 150% overloads for 15 secs. 3. Motor subject to reverse rotation shall be designed to withstand the stresses encountered when starting with non energized shaft rotating at 125% of rated speed in reverse direction. 4. Motor shall be provided with antifriction bearings, unless sleeve bearings are required by the Motor application. 5. The Motor shall be provided with rating Name plate as per Design Std. code applicable.
12 | Applicable Deliverables for Motors | 1) Motor Datasheet. 2) General arrangement drawing. 3) Starting Torque Vs Speed Curve. 4) P.F / Efficiency Vs Load Curve. 5) Thermal Withstand Current (Hot/Cold) Vs Time Curve. 6) Current Vs Speed Curve. 7) Starting time. 8) TB & wiring details for auxiliaries. 9) ITP for Motor Inspection. (Vendor to take Approval from Thermax QAC) 10) Above all documents to be submitted as Post PO by Vendor to Thermax. 11) Vendor to submit any other documents as required by Customer / Consultant without any delay & any commercial implications. 12) Terminal Box GA and Gland hole details. | 1) Motor Datasheet. 2) General arrangement drawing. 3) Starting Torque Vs Speed Curve. 4) P.F / Efficiency Vs Load Curve. 5) Thermal Withstand Current (Hot/Cold) Vs Time Curve. 6) Current Vs Speed Curve. 7) Starting time. 8) TB & wiring details for auxiliaries. 9) ITP for Motor Inspection. (Vendor to take Approval from Thermax QAC) 10) Above all documents to be submitted as Post PO by Vendor to Thermax. 11) Vendor to submit any other documents as required by Customer / Consultant without any delay & any commercial implications. 12) Terminal Box GA and Gland hole details.

## SAFE AREA MOTOR LIST
MOTOR LIST FOR SAFE AREA
SR.NO. | TAG. NO. | DESCRIPTION | WORKING/STANDBY | MOTOR RATING (kW) | RPM | TYPE OF MOUNTING | MOTOR FRAME SIZE | MOTOR GD2 (kg.m2) | GD2 of Driven Equipment | Bkw | TYPE OF COUPLING | LOCATION | VOLTAGE (volts) | FREQUENCY (Hz) | FEEDER TYPE | CABLE SIZE | SPACE HEATER | ROLLER BEARING | INSULATED BEARING | THERMISTOR | BEARING RTD | WINDING RTD | MOTOR ENERGY EFFICIENCY | FULL LOAD CURRENT | POWER FACTOR | MOTOR EFFICIENCY AT 100% | MAKE | PARTCODE | REMARK

## SAFE AREA MOTOR BOM
LT MOTOR BOM FOR SAFE AREA
Sr.No. | PARTCODE | DESCRIPTION | UNIT | QTY | REMARK

## HAZARDOUS AREA MOTOR LIST
MOTOR LIST FOR HAZARDOUS AREA
SR.NO. | TAG. NO. | DESCRIPTION | WORKING/STANDBY | MOTOR RATING (kW) | RPM | TYPE OF MOUNTING | MOTOR FRAME SIZE | MOTOR GD2 (kg.m2) | GD2 of Driven Equipment | BkW | TYPE OF COUPLING | LOCATION | VOLTAGE (volts) | FREQUENCY (Hz) | FEEDER TYPE | CABLE SIZE | SPACE HEATER | ROLLER BEARING | INSULATED BEARING | THERMISTOR | BEARING RTD | WINDING RTD | MOTOR ENERGY EFFICIENCY | FULL LOAD CURRENT | POWER FACTOR | MOTOR EFFICIENCY AT 100% | MAKE | PARTCODE | REMARK

## HAZARDOUS AREA MOTOR BOM
LT MOTOR BOM FOR HAZARDOUS AREA
Sr.No. | PARTCODE | DESCRIPTION | UNIT | QTY | REMARK