## COVER
THERMAX LIMITED
HEATING
PUNE — 411 019
| TITLE |  | LPBS SPECIFICATION AND LIST
CLIENT
| CONSULTANT |  | THERMAX PROJECT HEATING
| PROJECT |  | TEST-05-11-2024
| THERMAX O.C. NO. |  | OC NO-05-11-2024
THERMAX DOC. NO. / CLIENT DOC. NO.
ISSUED FOR APPROVAL
| REV NO. | DATE | DESCRIPTION | PREPD. BY | CHKD. BY | APPD. BY | 5.5

## INSTRUCTION PAGE
OC NO XXX -INSTRUCTIONS TO LOCAL PUSH BUTTON STATIONS VENDORS
OFFER :
Offer for the LPBS shall be based on following documents enclosed.
Sr No. | Document Title | Document No | Total Pages
1 | LPBS Technical Specifications | ------ | Sheet
2 | LPBS List | ------ | Sheet
3 | GAD | ------ | Sheet
4 | Deviation format | ------ | Sheet
The offer shall be strictly based on the document mentioned above. Deviations if any shall be clearly highlighted in the offer in the deviations format enclosed, otherwise it is presumed that there is no deviation. Vendor shall obtain the necessary clarity from Thermax regarding the discrepancy if any in the specifications furnished. Technical literature shall be furnished along with the offer. Vendor shall enclose along with his offer the purchase specifications of Thermax stamped as "Accepted ". Offer not in line with the above shall be summarily rejected. Offer complete in all respects should be received by us within 7 days from date of this enquiry.Offer complete in all respects should be received by us within 7 days from date of this enquiry.
B) DRAWING SUBMISSION :
Following documents shall be submitted to us for our / our client’s approval in '3' sets. However drawing submission, approval, inspection and / or certification does neither relieve the vendor of his responsibility for furnishing the equipment confirming to the requirement of purchase specification nor prejudice any claim.
Sr No. | ALONG WITH THE OFFER : | AFTER PLACEMENT OF ORDER | TIME
1 | G. A. of LPBS with dimensions | 1. LPBS GA, Wiring diagram, Legend details, BOM etc | AS PER P.O.
2 | Technical literature
3 | QAP | 2. Any other document/drawing as mentioned in specifications enclosed/ required by our client. | AS PER P.O.
4 | Stamped purchase specifications
5 | Deviation list ( if any )
The drawings submitted should be legible and correct as per specifications and should not call for resubmission.

## SPECIFICATION
LOCAL PUSH BUTTON STATION GENERAL SPECIFICATIONS:
| Specifications | LPBS for Safe Area | LPBS for Hazardous Area
1 | Type
2 | IP Protection
3 | Enclosure MOC & Thickness
4 | Quantity
5 | LPBS Colour Shade
6 | Cable Entry, Gland Plate Thickness
7 | Canopy
8 | Canopy Type
The Local Push Button Station shall have following components:
Push Button Colors:
1 | Start Push Button -
Forward Start Push Button -
Reverse Start Push Button -
Emergency Stop Button -
Speed increase Push Button –
Speed decrease Push Button -
ON Indication Lamp -
OFF Indication Lamp -
Push Button Configuration:
1 | Start Push Button
2 | Forward Start Push Button
3 | Reverse Start Push Button
4 | Emergency Stop Push button
5 | Analogue Ammeter
6 | Speed increase Push Button
7 | Speed decrease Push Button
8 | Analogue RPM Meter
9 | ON Indication Lamp
10 | OFF Indication Lamp
SPECIFICATION : -
1 | LPBS shall be Dust, Vermin & Oil tight proof, Neoprene Rubber gasketed.
2 | Each Push Button will have 2 NO + 2 NC contact assembly wired upto terminal.
3 | Contact rating for Push Button will be 5A @ 240 VAC / 110 VAC / 24 VDC, 50 Hz.
4 | All components shall be wired upto 4 mm2 terminals with extra flexible wires.
5 | Inscription plates shall be in English and should be corrosion resistant type.
6 | 20% spare capacity shall be provided on the terminal blocks
7 | Ammeter shall be 4 to 20 mA calibrated to speed range of driven equipment if applicable.
8 | CT ratio to be confirmed by MCC vendor. Same shall be updated later in this document.
9 | LPBS shall be provided with Inscription Plates of rear engraved perspex with white.
10 | Letters on Black Background. The Letter size shall be 6 mm.
11 | All Push button shall be provided with intergral escutcheon plates marked with it's function i.e. START / STOP etc.
12 | For Detail Specification, refer attached GAD of LPBS.
13 | Vendor to confirm RPM from Thermax before procurement .
14 | For Dual and Triple type, the LPBS enclosure shall be common.
15 | Identification of wire by numbered plastic / ceramic ferrules.
16 | Note : Certification & Documents 1. GA Drawing, Front, Elevations, cross sectional, Component & Fixing details for Engineering Approval. 2. Routine Test Certificate. 3. Ingress Protection Certification. 4. Model No. Details.
17 | LPBS shall be supplied with necessary GI mounting hardware.
18 | Cable Gland Excluded From Vendor scope of supply.
19 | Tag Plates for each LPBS Shall be of MOC traffolyte engraved with black letters on white background.

## LPBS LIST SAFE AREA
LPBS BOM LIST FOR SAFE AREA
SR.NO. | TAG. NO. | DESCRIPTION | kW RATING | LPBS TYPE | CANOPY REQUIRED | MOTOR LOCATION | GLAND SIZE | PART CODE | REMARK
1 | M-01 | PUMP-1 | 3.7 | TYPE-1 |  |  | 3/4" ET x 1 Nos
2 | M-02 | PUMP-2 | 3.7 | TYPE-2 |  |  | 3/4" ET x 1 Nos
3 | M-03 | PUMP-3 | 2.2 | TYPE-3 |  |  | 3/4" ET x 1 Nos
4 | M-04 | PUMP-4 | 2.2 | TYPE-4 |  |  | 3/4" ET x 1 Nos
5 | M-05 | PUMP-5 | 2.2 | TYPE-5 |  |  | 1" ET x 1 Nos
6 | M-06 | PUMP-6 | 2.2 | TYPE-6 |  |  | 3/4" ET x 1 Nos
7 | M-07 | PUMP-7 | 2.2 | TYPE-7 |  |  | 1" ET x 1 Nos
8 | M-08 | PUMP-8 | 2.2 | TYPE-8 |  |  | 3/4" ET x 1 Nos
9 | M-09 | PUMP-9 | 1.5 | TYPE-9 |  |  | 3/4" ET x 2 Nos
10 | M-10 | PUMP-10 | 1.5 | TYPE-10 |  |  | 3/4" ET x 3 Nos
11 | M-11 | PUMP-11 | 18.5 | TYPE-11 |  |  | 3/4" ET x 2 Nos
12 | M-12 | PUMP-12 | 18.5 | TYPE-12 |  |  | 3/4" ET x 1 Nos
16 | M-16 | PUMP-16 | 2.2 | TYPE-16 |  |  | 3/4" ET x 3 Nos
| 1 | Type Of LPBS |  |  | Nos
| 2 | Type Of LPBS |  |  | Nos
|  | Total |  |  | Nos

## LPBS LIST HAZARDOUS AREA
LPBS BOM LIST FOR HAZARDOUS AREA
SR.NO. | TAG. NO. | DESCRIPTION | kW RATING | LPBS TYPE | CANOPY REQUIRED | ZONE | GAS GROUP | TEMPARETURE CLASS | MOTOR LOCATION | GLAND SIZE | PART CODE | REMARK
1 | M-01 | PUMP-1 | 3.7 | TYPE-1 | [5 empty] | 3/4" ET x 1 Nos
2 | M-02 | PUMP-2 | 3.7 | TYPE-2 | [5 empty] | 3/4" ET x 1 Nos
3 | M-03 | PUMP-3 | 2.2 | TYPE-3 | [5 empty] | 3/4" ET x 1 Nos
4 | M-04 | PUMP-4 | 2.2 | TYPE-4 | [5 empty] | 3/4" ET x 1 Nos
5 | M-05 | PUMP-5 | 2.2 | TYPE-5 | [5 empty] | 1" ET x 1 Nos
6 | M-06 | PUMP-6 | 2.2 | TYPE-6 | [5 empty] | 3/4" ET x 1 Nos
7 | M-07 | PUMP-7 | 2.2 | TYPE-7 | [5 empty] | 1" ET x 1 Nos
8 | M-08 | PUMP-8 | 2.2 | TYPE-8 | [5 empty] | 3/4" ET x 1 Nos
9 | M-09 | PUMP-9 | 1.5 | TYPE-9 | [5 empty] | 3/4" ET x 2 Nos
10 | M-10 | PUMP-10 | 1.5 | TYPE-10 | [5 empty] | 3/4" ET x 3 Nos
11 | M-11 | PUMP-11 | 18.5 | TYPE-11 | [5 empty] | 3/4" ET x 2 Nos
12 | M-12 | PUMP-12 | 18.5 | TYPE-12 | [5 empty] | 3/4" ET x 1 Nos
13 | M-13 | PUMP-13 | 18.5 | TYPE-13 | [5 empty] | 3/4" ET x 2 Nos
14 | M-14 | PUMP-14 | 3.7 | TYPE-14 | [5 empty] | 3/4" ET x 2 Nos
15 | M-15 | PUMP-15 | 3.7 | TYPE-15 | [5 empty] | 3/4" ET x 2 Nos
16 | M-16 | PUMP-16 | 2.2 | TYPE-16 | [5 empty] | 3/4" ET x 3 Nos
| 1 | Type Of LPBS |  |  | Nos
| 2 | Type Of LPBS |  |  | Nos
|  | Total |  |  | Nos

## SELECTION CRITERIA
LOCAL PUSH BUTTON STATION | [9 empty] | WWS STD. PART CODE MOC WISE |  |  |  | CABLE CORE/SIZE (minimum core requirement) |  |  |  |  | DESCRIPTION
Sr. No. | Type of LPBS | Start Push Button | Emergency Stop Push Button | ON Indication Lamp | OFF Indication Lamp | Local/Remote Selector Switch | Speed increase & decrease Push Button (DC) | Analogue Ammeter (Amp) | Analogue RPM Meter (mA) | Diecast MOC | FRP MOC | CRCA MOC | SS304 MOC | Cable Entry From Bottom HEATING | HEATING | WWS-SPG | WWS-IPG | ENVIRO | HEATING
1 | TYPE-1 | NA | Emergency Stop Push button | NA | NA | NA | NA | NA | NA | WAFAA11001 | WAFAA12001 | WAFAA13001 | WAFAA14001 | 3/4 " X 1 Nos | 2Cx1.5mm2 | 2Cx1.5mm2 | 3Cx1.5mm2 |  | STOP COMMAND FROM LCS
| TYPE-2 | Start Push Button | Emergency Stop Push button | NA | NA | NA | NA | NA | NA | WAFAA11002 | WAFAA12002 | WAFAA13002 | WAFAA14002 | 3/4 " X 1 Nos | 4Cx1.5mm2 | 4Cx1.5mm2 | 5Cx1.5mm2 |  | START COMMAND FROM LCS STOP COMMAND FROM LCS
| TYPE-3 | Forward Start Push Button Reverse Start Push Button | Emergency Stop Push button | NA | NA | NA | NA | NA | NA |  |  |  |  | 3/4 " X 1 Nos | 6Cx1.5mm2 |  | 7Cx1.5mm2 |  | FORWARD START COMMAND FROM LCS REVERSE START COMMAND FROM LCS STOP COMMAND FROM LCS
| TYPE-4 | Start Push Button | Emergency Stop Push button | NA | NA | YES | NA | NA | NA |  |  |  |  | 3/4 " X 1 Nos | 6Cx1.5mm2 | 7Cx1.5mm2 | 7Cx1.5mm2 |  | START COMMAND FROM LCS STOP COMMAND FROM LCS LOCAL/ REMOTE SELECTOR SWITCH
| TYPE-5 | Forward Start Push Button Reverse Start Push Button | Emergency Stop Push button | NA | NA | YES | NA | NA | NA |  |  |  |  | 3/4 " X 1 Nos | 8Cx1.5mm2 | 12Cx1.5mm2 | 10Cx1.5mm2 |  | FORWARD START COMMAND FROM LCS REVERSE START COMMAND FROM LCS STOP COMMAND FROM LCS LOCAL/ REMOTE SELECTOR SWITCH
| TYPE-6 | Start Push Button | Emergency Stop Push button | NA | NA | NA | YES | NA | NA |  |  |  |  | 3/4 " X 2 Nos | 4Cx1.5mm2 4Cx0.5mm2 |  | 10Cx1.5mm2 |  | START COMMAND FROM LCS STOP COMMAND FROM LCS SPEED INCREASE FROM LCS SPEED DECREASE FROM LCS
| TYPE-7 | Forward Start Push Button Reverse Start Push Button | Emergency Stop Push button | NA | NA | NA | YES | NA | NA |  |  |  |  | 3/4 " X 2 Nos | 6Cx1.5mm2 4Cx0.5mm2 |  | 10Cx1.5mm2 |  | FORWARD START COMMAND FROM LCS REVERSE START COMMAND FROM LCS STOP COMMAND FROM LCS SPEED INCREASE FROM LCS SPEED DECREASE FROM LCS
| TYPE-8 | Forward Start Push Button Reverse Start Push Button | Emergency Stop Push button | NA | NA | YES | YES | NA | NA |  |  |  |  | 1" X 1 Nos | 12Cx1.5mm2 | 12Cx1.5mm2 | 12Cx1.5mm2 |  | FORWARD START COMMAND FROM LCS REVERSE START COMMAND FROM LCS STOP COMMAND FROM LCS LOCAL/ REMOTE SELECTOR SWITCH SPEED INCREASE FROM LCS SPEED DECREASE FROM LCS
| TYPE-9 | Start Push Button | Emergency Stop Push button | YES | YES | NA | NA | NA | NA | WAFAA11003 | WAFAA12003 | WAFAA13003 | WAFAA14003 | 3/4 " X 1 Nos | 8Cx1.5mm2 | 12Cx1.5mm2 | 10Cx1.5mm2 |  | START COMMAND FROM LCS WITH INDICATION STOP COMMAND FROM LCS WITH INDICATION
| TYPE-10 | Start Push Button | Emergency Stop Push button | YES | YES | YES | NA | NA | NA | WAFAA11005 | WAFAA12005 | WAFAA13005 | WAFAA14005 | 1" X 1 Nos | 10Cx1.5mm2 | 12Cx1.5mm2 | 12Cx1.5mm2 |  | START COMMAND FROM LCS WITH INDICATION STOP COMMAND FROM LCS WITH INDICATION LOCAL/ REMOTE SELECTOR SWITCH
| TYPE-11 | Forward Start Push Button Reverse Start Push Button | Emergency Stop Push button | NA | NA | NA | YES | NA | YES |  |  |  |  | 3/4 " X 3 Nos | 6Cx1.5mm2 4Cx0.5mm2 1Px0.5mm2 SHILEDED CABLES |  | 10Cx1.5mm2 1P X 1.5 mm2 SHILEDED CABLES |  | FORWARD START COMMAND FROM LCS REVERSE START COMMAND FROM LCS STOP COMMAND FROM LCS SPEED INCREASE FROM LCS SPEED DECREASE FROM LCS SPEED FEEDBACK FROM LCS
| TYPE-12 | Start Push Button | Emergency Stop Push button | NA | NA | NA | NA | YES | NA |  |  |  |  | 3/4 " X 1 Nos | 6Cx1.5mm2 |  | 5Cx1.5mm2 1P X 1.5 mm2 SHILEDED CABLES |  | START COMMAND FROM LCS STOP COMMAND FROM LCS CURRENT FEEDBACK FROM LCS
| TYPE-13 | Start Push Button | Emergency Stop Push button | NA | NA | NA | NA | NA | YES |  |  |  |  | 3/4 " X 2 Nos | 4Cx1.5mm2 1Px0.5mm2 SHILEDED CABLES |  | 5Cx1.5mm2 1P X 1.5 mm2 SHILEDED CABLES |  | START COMMAND FROM LCS STOP COMMAND FROM LCS SPEED FEEDBACK FROM LCS
| TYPE-14 | Start Push Button | Emergency Stop Push button | NA | NA | NA | YES | YES | NA |  |  |  |  | 3/4 " X 2 Nos | 6Cx1.5mm2 4Cx0.5mm2 |  | 10Cx1.5mm2 1P X 1.5 mm2 SHILEDED CABLES |  | START COMMAND FROM LCS STOP COMMAND FROM LCS SPEED INCREASE FROM LCS SPEED DECREASE FROM LCS CURRENT FEEDBACK FROM LCS
| TYPE-15 | Start Push Button | Emergency Stop Push button | NA | NA | NA | NA | YES | YES |  |  |  |  | 3/4 " X 2 Nos | 6Cx1.5mm2 1Px0.5mm2 SHILEDED CABLES |  | 5Cx1.5mm2 2R X 1P X 1.5 mm2 SHILEDED CABLES |  | START COMMAND FROM LCS STOP COMMAND FROM LCS CURRENT FEEDBACK FROM LCS SPEED FEEDBACK FROM LCS
| TYPE-16 | Start Push Button | Emergency Stop Push button | NA | NA | NA | YES | YES | YES |  |  |  |  | 3/4 " X 3 Nos | 6Cx1.5mm2 4Cx0.5mm2 1Px0.5mm2 SHILEDED CABLES |  | 10Cx1.5mm2 2R X 1P X 1.5 mm2 SHILEDED CABLES |  | START COMMAND FROM LCS STOP COMMAND FROM LCS SPEED INCREASE FROM LCS SPEED DECREASE FROM LCS CURRENT FEEDBACK FROM LCS SPEED FEEDBACK FROM LCS
| TYPE-17 | NA | Stop - Red Color (rotate to release) | NA | NA | NA | NA | NA | NA | WAFAA11001 | WAFAA12001 | WAFAA13001 | WAFAA14001 |  |  | 2Cx1.5mm2 | 3Cx1.5mm2 |  |  | TYPE 17-29 not applicable for Heating
| TYPE-18 | Start | Stop - Red Color (rotate to release) | NA | NA | NA | NA | NA | NA | WAFAA11002 | WAFAA12002 | WAFAA13002 | WAFAA14002 |  |  | 4Cx1.5mm2 | 5Cx1.5mm2
| TYPE-19 | Start | Stop - Red Color (rotate to release) | NA | NA | NA | YES | NA | NA | [7 empty] | 10Cx1.5mm2
| TYPE-20 | Start | Stop - Red Color (rotate to release) | NA | NA | NA | NA | YES | NA | [7 empty] | 5Cx1.5mm2 1P X 1.5 mm2 SHILEDED CABLES
| TYPE-21 | Start | Stop - Red Color (rotate to release) | NA | NA | NA | NA | NA | YES | [7 empty] | 5Cx1.5mm2 1P X 1.5 mm2 SHILEDED CABLES
| TYPE-22 | Start | Stop - Red Color (rotate to release) | NA | NA | NA | YES | YES | NA | [7 empty] | 10Cx1.5mm2 1P X 1.5 mm2 SHILEDED CABLES
| TYPE-23 | Start | Stop - Red Color (rotate to release) | NA | NA | NA | NA | YES | YES | [7 empty] | 5Cx1.5mm2 2R X 1P X 1.5 mm2 SHILEDED CABLES
| TYPE-24 | Start | Stop - Red Color (rotate to release) | NA | NA | NA | YES | YES | YES | [7 empty] | 10Cx1.5mm2 2R X 1P X 1.5 mm2 SHILEDED CABLES
| TYPE-25 | Start | Stop - Red Color (rotate to release) | YES | YES | NA | NA | NA | NA | WAFAA11003 | WAFAA12003 | WAFAA13003 | WAFAA14003 |  |  | 12Cx1.5mm2 | 10Cx1.5mm2
| TYPE-26 | Start | Stop - Red Color (rotate to release) | NA | NA | YES | NA | NA | NA | WAFAA11004 | WAFAA12004 | WAFAA13004 | WAFAA14004 |  |  | 7Cx1.5mm2 | 7Cx1.5mm2
| TYPE-27 | Start | Stop - Red Color (rotate to release) | YES | YES | YES | NA | NA | NA | WAFAA11005 | WAFAA12005 | WAFAA13005 | WAFAA14005 |  |  | 12Cx1.5mm2 | 12Cx1.5mm2
| TYPE-28 | Start - Dual | Stop - Red Color (rotate to release) - Dual | NA | NA | NA | NA | NA | NA | WAFAA11006 | WAFAA12006 | WAFAA13006 | WAFAA14006 |  |  | 12Cx1.5mm2
| TYPE-29 | Start - Triple | Stop - Red Color (rotate to release) - Triple | NA | NA | NA | NA | NA | NA | WAFAA11007 | WAFAA12007 | WAFAA13007 | WAFAA14007 |  |  | 12Cx1.5mm2
Make of Components:
1 | All components shall be As per approved vendor list